## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Vector
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Vector
[15 empty] | For Year Ended | Combined
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | 34020 | MEAS K17 - K17 GRAEME AVE | Auckland | MEAS K17 | 2024-04-01 | 45383.2792 | 2024-04-01 | 45383.5451 | 0.20162 | 0.0028003 | 1753 | 126212 | Unplanned | Defective equipment
10 |  | 34021 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-01 | 45383.5764 | 2024-04-01 | 45383.8993 | 0.0034218 | 2.8754e-05 | 9 | 2142 | Unplanned | Defective equipment
11 |  | 34022 | PAPA K09 - K09 LAURIE AVE | Auckland | PAPA K09 | 2024-04-02 | 45384.1667 | 2024-04-02 | 45384.2278 | 0.041419 | 0.00049681 | 311 | 25928 | Planned | Planned
12 |  | 34023 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-04-02 | 45384.0778 | 2024-04-02 | 45384.1354 | 0.00039777 | 4.792e-06 | 3 | 249 | Unplanned | Defective equipment
13 |  | 34027 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-02 | 45384.375 | 2024-04-02 | 45384.7111 | 0.095873 | 0.00019808 | 124 | 60016 | Planned | Planned
14 |  | 34028 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-02 | 45384.375 | 2024-04-02 | 45384.3861 | 7.6678e-05 | 4.792e-06 | 3 | 48 | Planned | Planned
15 |  | 34029 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-04-02 | 45384.3757 | 2024-04-02 | 45384.6514 | 0.034881 | 8.7859e-05 | 55 | 21835 | Planned | Planned
16 |  | 34030 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-02 | 45384.3785 | 2024-04-02 | 45384.6632 | 0.0013099 | 3.194e-06 | 2 | 820 | Planned | Planned
17 |  | 34031 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-02 | 45384.3958 | 2024-04-02 | 45384.6875 | 0.0080512 | 1.9167e-05 | 12 | 5040 | Planned | Planned
18 |  | 34032 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-04-02 | 45384.4174 | 2024-04-02 | 45384.6354 | 0.042135 | 0.00013419 | 84 | 26376 | Planned | Planned
19 |  | 34034 | WIRI K19 - K19 WIRI STATION RD | Auckland | WIRI K19 | 2024-04-02 | 45384.4306 | 2024-04-04 | 45386.75 | 0.010655 | 6.39e-06 | 2 | 6670 | Unplanned | Defective equipment
20 |  | 34035 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-04-02 | 45384.3986 | 2024-04-02 | 45384.6368 | 0.027396 | 7.9871e-05 | 50 | 17150 | Planned | Planned
21 |  | 34036 | ORAK K05 - K05 GODDEN CRES | Auckland | ORAK K05 | 2024-04-02 | 45384.7181 | 2024-04-02 | 45384.8319 | 0.019387 | 0.00011821 | 74 | 12136 | Unplanned | Cause unknown
22 |  | 34037 | HCRE K12 - K12 OCEAN VIEW ROAD | Northern | HCRE K12 | 2024-04-03 | 45385.0417 | 2024-04-03 | 45385.1007 | 0.0012221 | 1.4376e-05 | 9 | 765 | Planned | Planned
23 |  | 34038 | ORAK K05 - K05 GODDEN CRES | Auckland | ORAK K05 | 2024-04-03 | 45385.2611 | 2024-04-03 | 45385.2917 | 0.0039361 | 8.9458e-05 | 56 | 2464 | Unplanned | Cause unknown
24 |  | 34039 | KKAP K06 - K06 PEAK RD | Northern | KKAP K06 | 2024-04-03 | 45385.3764 | 2024-04-03 | 45385.6097 | 0.0048307 | 1.4377e-05 | 9 | 3024 | Planned | Planned
25 |  | 34040 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-04-03 | 45385.3347 | 2024-04-03 | 45385.6243 | 0.00066614 | 1.597e-06 | 1 | 417 | Planned | Planned
26 |  | 34041 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-04-03 | 45385.375 | 2024-04-03 | 45385.6736 | 0.0027476 | 6.39e-06 | 4 | 1720 | Planned | Planned
27 |  | 34042 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-03 | 45385.3757 | 2024-04-03 | 45385.6139 | 0.0065751 | 1.9166e-05 | 12 | 4116 | Planned | Planned
28 |  | 34043 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-03 | 45385.3597 | 2024-04-03 | 45385.6347 | 0.029099 | 7.3481e-05 | 46 | 18216 | Planned | Planned
29 |  | 34044 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-04-03 | 45385.5972 | 2024-04-03 | 45385.6146 | 3.9936e-05 | 1.597e-06 | 1 | 25 | Unplanned | Other Cause | Outage caused by Tap Operation
30 |  | 34045 | BIRK K11 - K11 BEACH HAVEN | Northern | BIRK K11 | 2024-04-03 | 45385.7833 | 2024-04-03 | 45385.8556 | 0.012959 | 0.0001246 | 78 | 8112 | Unplanned | Wildlife
31 |  | 34046 | GREE K11 - K11 CRYERS ROAD | Auckland | GREE K11 | 2024-04-03 | 45385.966 | 2024-04-04 | 45386.0729 | 0.0017221 | 1.1182e-05 | 7 | 1078 | Planned | Planned
32 |  | 34047 | GREE K08 - K08 GREENMOUNT DRIVE VIA LS | Auckland | GREE K08 | 2024-04-04 | 45386.0104 | 2024-04-04 | 45386.0354 | 0.00028754 | 7.987e-06 | 5 | 180 | Planned | Planned
33 |  | 34048 | PAPA K09 - K09 LAURIE AVE | Auckland | PAPA K09 | 2024-04-04 | 45386.1667 | 2024-04-04 | 45386.2271 | 0.043222 | 0.00049681 | 311 | 27057 | Planned | Planned
34 |  | 34049 | BMON K09 - K09 BAYSWATER | Northern | BMON K09 | 2024-04-04 | 45386.3549 | 2024-04-04 | 45386.5472 | 0.090712 | 0.00032748 | 205 | 56785 | Planned | Planned
35 |  | 34050 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-04-04 | 45386.375 | 2024-04-04 | 45386.6771 | 0.068795 | 0.00015815 | 99 | 43065 | Planned | Planned
36 |  | 34051 | RANU K05 - K05 ARMADA DRIVE | Northern | RANU K05 | 2024-04-04 | 45386.375 | 2024-04-04 | 45386.5903 | 0.12628 | 0.00040735 | 255 | 79050 | Planned | Planned
37 |  | 34052 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-04-04 | 45386.3771 | 2024-04-04 | 45386.6181 | 0.0085352 | 2.5558e-05 | 16 | 5343 | Planned | Planned
38 |  | 34053 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-04-04 | 45386.3958 | 2024-04-04 | 45386.5938 | 0.12611 | 0.00044249 | 277 | 78945 | Planned | Planned
39 |  | 34054 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-04 | 45386.4257 | 2024-04-04 | 45386.8021 | 0.00086582 | 1.597e-06 | 1 | 542 | Planned | Planned
40 |  | 34055 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-04-04 | 45386.4861 | 2024-04-04 | 45386.4896 | 0.0005032 | 0.00010064 | 63 | 315 | Unplanned | Other Cause | Outage caused by Tap Operation
41 |  | 34056 | PAPA K01 - K01 SETTLEMENT RD | Auckland | PAPA K01 | 2024-04-04 | 45386.5667 | 2024-04-04 | 45386.8319 | 0.12876 | 0.00033706 | 211 | 80602 | Unplanned | Third party interference
42 |  | 34057 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-04-04 | 45386.375 | 2024-04-04 | 45386.6299 | 0.0064489 | 1.7571e-05 | 11 | 4037 | Planned | Planned
43 |  | 34058 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-04-04 | 45386.7014 | 2024-04-05 | 45387.6125 | 0.2372 | 0.00035464 | 222 | 148484 | Unplanned | Defective equipment
44 |  | 34059 | WAIA K04 - K04 CAPRICORN PLACE | Northern | WAIA K04 | 2024-04-04 | 45386.9792 | 2024-04-05 | 45387.1083 | 0.0065128 | 3.5144e-05 | 22 | 4077 | Planned | Planned
45 |  | 34060 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2024-04-04 | 45386.9799 | 2024-04-05 | 45387.1076 | 0.0079362 | 4.3131e-05 | 27 | 4968 | Planned | Planned
46 |  | 34061 | PAKU K13 - K13 THE BOULEVARD | Auckland | PAKU K13 | 2024-04-05 | 45387.125 | 2024-04-05 | 45387.2333 | 0.015398 | 0.00025879 | 81 | 9639 | Planned | Planned
47 |  | 34062 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-04-05 | 45387.2757 | 2024-04-05 | 45387.691 | 0.33035 | 0.003238 | 1221 | 206800 | Unplanned | Defective equipment
48 |  | 34062 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K09 | 2024-04-05 | 45387.2757 | 2024-04-05 | 45387.691 | 0.041975 | 0.00091216 | 356 | 26276 | Unplanned | Defective equipment
49 |  | 34065 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-04-05 | 45387.375 | 2024-04-05 | 45387.6389 | 0.0030352 | 7.987e-06 | 5 | 1900 | Planned | Planned
50 |  | 34066 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-05 | 45387.4035 | 2024-04-05 | 45387.7222 | 0.057192 | 0.00012459 | 78 | 35802 | Planned | Planned
51 |  | 34067 | MANU K10 - K10 RUSSELL RD | Auckland | MANU K10 | 2024-04-05 | 45387.3958 | 2024-04-05 | 45387.7014 | 0.31549 | 0.00073643 | 461 | 197496 | Planned | Planned
52 |  | 34068 | MNAB K03 - K03 LEONARD RD | Auckland | MNAB K03 | 2024-04-05 | 45387.65 | 2024-04-05 | 45387.8458 | 0.11019 | 0.0019329 | 995 | 68978 | Unplanned | Defective equipment
53 |  | 34069 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-05 | 45387.6708 | 2024-04-05 | 45387.6799 | 0.0039425 | 0.00030514 | 191 | 2468 | Planned | Planned
54 |  | 34070 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-04-05 | 45387.7049 | 2024-04-05 | 45387.7757 | 0.0011406 | 1.1181e-05 | 7 | 714 | Unplanned | Defective equipment
55 |  | 34071 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-04-06 | 45388.0167 | 2024-04-06 | 45388.0694 | 0.031214 | 0.0015096 | 945 | 19540 | Unplanned | Cause unknown
56 |  | 34072 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-04-06 | 45388.2917 | 2024-04-06 | 45388.6771 | 0.064426 | 0.00090415 | 394 | 40330 | Unplanned | Cause unknown
57 |  | 34073 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-04-06 | 45388.3569 | 2024-04-06 | 45388.6333 | 0.0012716 | 3.195e-06 | 2 | 796 | Planned | Planned
58 |  | 34074 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2024-04-06 | 45388.3354 | 2024-04-06 | 45388.6736 | 0.1058 | 0.00021725 | 136 | 66232 | Planned | Planned
59 |  | 34075 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-06 | 45388.375 | 2024-04-06 | 45388.6528 | 0.00063898 | 1.597e-06 | 1 | 400 | Planned | Planned
60 |  | 34076 | CHEV K04 - K04 MOA RD | Auckland | CHEV K04 | 2024-04-06 | 45388.375 | 2024-04-06 | 45388.541 | 0.17181 | 0.00071886 | 450 | 107550 | Planned | Planned
61 |  | 34077 | WAIM K03 - K03 REWITI | Northern | WAIM K03 | 2024-04-06 | 45388.3764 | 2024-04-06 | 45388.6007 | 0.021155 | 6.5493e-05 | 41 | 13243 | Planned | Planned
62 |  | 34078 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-06 | 45388.3542 | 2024-04-06 | 45388.5625 | 0.0047924 | 1.5975e-05 | 10 | 3000 | Unplanned | Defective equipment
63 |  | 34080 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-04-06 | 45388.375 | 2024-04-06 | 45388.6396 | 0.0085208 | 2.2364e-05 | 14 | 5334 | Planned | Planned
64 |  | 34081 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-04-06 | 45388.384 | 2024-04-06 | 45388.684 | 0.40095 | 0.00092811 | 581 | 250992 | Planned | Planned
65 |  | 34082 | REMU K11 - K11 LUCERNE RD | Auckland | REMU K11 | 2024-04-06 | 45388.4437 | 2024-04-06 | 45388.4444 | 0.00058307 | 0.00058307 | 365 | 365 | Unplanned | Human error
66 |  | 34082 | REMU K11 - K11 LUCERNE RD | Auckland | REMU K17 | 2024-04-06 | 45388.4437 | 2024-04-06 | 45388.4444 | 0.0026821 | 0.0026821 | 1679 | 1679 | Unplanned | Human error
67 |  | 34083 | OREW K10 - K10 HATFIELDS | Northern | OREW K10 | 2024-04-06 | 45388.9931 | 2024-04-06 | 45388.9958 | 0.00015336 | 3.8339e-05 | 24 | 96 | Unplanned | Wildlife
68 |  | 34084 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-04-06 | 45388.709 | 2024-04-06 | 45388.8229 | 0.00026198 | 1.597e-06 | 1 | 164 | Unplanned | Cause unknown
69 |  | 34085 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-04-07 | 45389.375 | 2024-04-07 | 45389.4035 | 0.0077285 | 0.0001885 | 118 | 4838 | Unplanned | Defective equipment
70 |  | 34087 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-04-07 | 45389.6667 | 2024-04-07 | 45389.8208 | 0.0042556 | 1.9169e-05 | 12 | 2664 | Unplanned | Cause unknown
71 |  | 34088 | SHOW K03 - K03 MEADOWLAND DR | Auckland | SHOW K03 | 2024-04-07 | 45389.9792 | 2024-04-08 | 45390.1299 | 0.044371 | 0.00020447 | 128 | 27776 | Planned | Planned
72 |  | 34089 | HVAL K02 - K02 CORBAN AVENUE | Northern | HVAL K02 | 2024-04-08 | 45390.2583 | 2024-04-08 | 45390.3903 | 0.0074346 | 3.9937e-05 | 25 | 4654 | Planned | Planned
73 |  | 34090 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-04-08 | 45390.3965 | 2024-04-08 | 45390.7021 | 0.0049202 | 1.1182e-05 | 7 | 3080 | Planned | Planned
74 |  | 34091 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-04-08 | 45390.4201 | 2024-04-08 | 45390.6917 | 0.0018738 | 4.792e-06 | 3 | 1173 | Planned | Planned
75 |  | 34092 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-08 | 45390.3757 | 2024-04-10 | 45392.6687 | 0.25231 | 0.00064218 | 188 | 157944 | Planned | Planned
76 |  | 34093 | MWES K10 - K10 KIWI HARVEST | Auckland | MWES K10 | 2024-04-08 | 45390.4 | 2024-04-08 | 45390.6389 | 0.0021981 | 6.389e-06 | 4 | 1376 | Planned | Planned
77 |  | 34094 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-04-08 | 45390.4306 | 2024-04-08 | 45390.6667 | 0.0054314 | 1.5974e-05 | 10 | 3400 | Planned | Planned
78 |  | 34095 | HELE K12 - K12 LOCAL SERVICE | Northern | HELE K12 | 2024-04-03 | 45385.3569 | 2024-04-03 | 45385.3819 | 5.7509e-05 | 1.597e-06 | 1 | 36 | Planned | Planned
79 |  | 34096 | HELE K12 - K12 LOCAL SERVICE | Northern | HELE K12 | 2024-04-08 | 45390.4854 | 2024-04-08 | 45390.5069 | 4.9521e-05 | 1.597e-06 | 1 | 31 | Planned | Planned
80 |  | 34097 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-08 | 45390.4507 | 2024-04-08 | 45390.6625 | 0.057678 | 0.0007508 | 470 | 36106 | Unplanned | Cause unknown
81 |  | 34098 | SIMP K07 - K07 BABICH RD | Northern | SIMP K07 | 2024-04-08 | 45390.6514 | 2024-04-08 | 45390.6562 | 0.00029074 | 4.1534e-05 | 26 | 182 | Unplanned | Other Cause | Outage caused by Tap Operation
82 |  | 34100 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-04-08 | 45390.675 | 2024-04-08 | 45390.7083 | 0.0030671 | 6.3898e-05 | 40 | 1920 | Unplanned | Cause unknown
83 |  | 34101 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-04-08 | 45390.7319 | 2024-04-08 | 45390.7438 | 0.00013578 | 7.987e-06 | 5 | 85 | Unplanned | Other Cause | Outage caused by Tap Operation
84 |  | 34102 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2024-04-08 | 45390.8389 | 2024-04-09 | 45391.0104 | 0.016967 | 6.8691e-05 | 43 | 10621 | Unplanned | Defective equipment
85 |  | 34103 | SHOW K02 - K02 GILLET PL | Auckland | SHOW K02 | 2024-04-08 | 45390.9583 | 2024-04-09 | 45391.0417 | 0.016677 | 0.00013898 | 87 | 10440 | Planned | Planned
86 |  | 34104 | HOWI K12 - K12 MACLEANS RD | Auckland | HOWI K12 | 2024-04-09 | 45391.0833 | 2024-04-09 | 45391.1701 | 0.008187 | 6.5495e-05 | 41 | 5125 | Planned | Planned
87 |  | 34105 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-04-09 | 45391.2917 | 2024-04-09 | 45391.716 | 0.15868 | 0.0020607 | 645 | 99330 | Planned | Planned
88 |  | 34106 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-04-09 | 45391.3333 | 2024-04-09 | 45391.6958 | 0.033551 | 0.00062942 | 199 | 21003 | Planned | Planned
89 |  | 34108 | HBUR K03 - K03 MAHARA AVE + LS | Northern | HBUR K03 | 2024-04-09 | 45391.3333 | 2024-04-09 | 45391.6882 | 0.036734 | 7.1886e-05 | 45 | 22995 | Planned | Planned
90 |  | 34109 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-04-09 | 45391.3542 | 2024-04-09 | 45391.6417 | 0.05886 | 0.00014217 | 89 | 36846 | Planned | Planned
91 |  | 34111 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-04-09 | 45391.3778 | 2024-04-09 | 45391.6514 | 0.009441 | 2.3962e-05 | 15 | 5910 | Planned | Planned
92 |  | 34112 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-09 | 45391.4028 | 2024-04-09 | 45391.6944 | 0.074474 | 0.00017731 | 111 | 46620 | Planned | Planned
93 |  | 34113 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-09 | 45391.3639 | 2024-04-10 | 45392.659 | 0.11181 | 0.0014761 | 469 | 69994 | Unplanned | Defective equipment
94 |  | 34114 | HVAL K03 - K03 BRUCE McLAREN | Northern | HVAL K02 | 2024-04-09 | 45391.5215 | 2024-04-09 | 45391.5625 | 0.0077285 | 0.000131 | 82 | 4838 | Unplanned | Defective equipment
95 |  | 34114 | HVAL K03 - K03 BRUCE McLAREN | Northern | HVAL K03 | 2024-04-09 | 45391.5215 | 2024-04-09 | 45391.5625 | 0.097344 | 0.0023067 | 1444 | 60937 | Unplanned | Defective equipment
96 |  | 34115 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-04-09 | 45391.3965 | 2024-04-09 | 45391.6424 | 0.037323 | 0.00010543 | 66 | 23364 | Planned | Planned
97 |  | 34116 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-09 | 45391.7312 | 2024-04-09 | 45391.7368 | 8.9458e-05 | 1.1182e-05 | 7 | 56 | Unplanned | Other Cause | Outage caused by Tap Operation
98 |  | 34117 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-04-09 | 45391.8299 | 2024-04-10 | 45392.05 | 0.2418 | 0.0039122 | 2449 | 151367 | Unplanned | Third party interference
99 |  | 34118 | SJOH K11 - K11 COLLEGE RD | Auckland | SJOH K11 | 2024-04-09 | 45391.9792 | 2024-04-10 | 45392.1236 | 0.11563 | 0.00055592 | 348 | 72384 | Planned | Planned
100 |  | 34119 | HCRE K12 - K12 OCEAN VIEW ROAD | Northern | HCRE K12 | 2024-04-10 | 45392.0417 | 2024-04-10 | 45392.0771 | 0.00073323 | 1.4376e-05 | 9 | 459 | Planned | Planned
101 |  | 34121 | GREE K11 - K11 CRYERS ROAD | Auckland | GREE K11 | 2024-04-10 | 45392.0424 | 2024-04-10 | 45392.1799 | 0.0022141 | 1.1182e-05 | 7 | 1386 | Planned | Planned
102 |  | 34122 | WIRI K18 - K18 ASH RD | Auckland | WIRI K18 | 2024-04-10 | 45392.2299 | 2024-04-10 | 45392.2688 | 0.00017892 | 3.195e-06 | 2 | 112 | Planned | Planned
103 |  | 34123 | TORB K08 - K08 GLENVAR ROAD | Northern | TORB K08 | 2024-04-10 | 45392.3542 | 2024-04-10 | 45392.7083 | 0.42935 | 0.00084186 | 527 | 268770 | Planned | Planned
104 |  | 34124 | ORAT K06 - K06 GLENGARRY ROAD | Northern | ORAT K06 | 2024-04-10 | 45392.3549 | 2024-04-10 | 45392.6917 | 0.044937 | 9.2653e-05 | 58 | 28130 | Planned | Planned
105 |  | 34125 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-04-10 | 45392.375 | 2024-04-10 | 45392.6472 | 0.09853 | 0.000254 | 159 | 61679 | Planned | Planned
106 |  | 34126 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-10 | 45392.3757 | 2024-04-10 | 45392.7438 | 0.038946 | 7.3481e-05 | 46 | 24380 | Planned | Planned
107 |  | 34127 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-04-10 | 45392.375 | 2024-04-10 | 45392.7431 | 0.060112 | 0.00011342 | 71 | 37630 | Planned | Planned
108 |  | 34128 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-04-10 | 45392.375 | 2024-04-10 | 45392.6875 | 0.015096 | 3.3546e-05 | 21 | 9450 | Planned | Planned
109 |  | 34129 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-04-10 | 45392.375 | 2024-04-10 | 45392.6375 | 0.033815 | 8.9458e-05 | 56 | 21168 | Planned | Planned
110 |  | 34130 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-10 | 45392.3896 | 2024-04-10 | 45392.6306 | 0.001663 | 4.792e-06 | 3 | 1041 | Planned | Planned
111 |  | 34131 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-10 | 45392.4201 | 2024-04-10 | 45392.6271 | 0.017614 | 5.9104e-05 | 37 | 11026 | Planned | Planned
112 |  | 34132 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-04-10 | 45392.4167 | 2024-04-10 | 45392.6076 | 0.0070288 | 2.5557e-05 | 16 | 4400 | Planned | Planned
113 |  | 34133 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-04-10 | 45392.4299 | 2024-04-10 | 45392.6458 | 0.012917 | 4.1532e-05 | 26 | 8086 | Planned | Planned
114 |  | 34134 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-04-10 | 45392.4174 | 2024-04-10 | 45392.7063 | 0.019936 | 4.7922e-05 | 30 | 12480 | Planned | Planned
115 |  | 34135 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-04-10 | 45392.5931 | 2024-04-10 | 45392.6493 | 0.00012939 | 1.597e-06 | 1 | 81 | Unplanned | Cause unknown
116 |  | 34138 | SHOW K06 - K06 FIELDSTONE COURT | Auckland | SHOW K06 | 2024-04-10 | 45392.9792 | 2024-04-11 | 45393.1306 | 0.057112 | 0.00026198 | 164 | 35752 | Planned | Planned
117 |  | 34139 | ONEH K02 - K02 - GALWAY ST | Auckland | ONEH K02 | 2024-04-11 | 45393.0417 | 2024-04-11 | 45393.0944 | 0.00072844 | 9.584e-06 | 6 | 456 | Planned | Planned
118 |  | 34140 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-04-11 | 45393.3028 | 2024-04-11 | 45393.3924 | 0.02874 | 0.0005 | 313 | 17991 | Unplanned | Vegetation
119 |  | 34142 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-11 | 45393.3611 | 2024-04-11 | 45393.4493 | 0.03462 | 0.0011135 | 642 | 21672 | Unplanned | Vegetation
120 |  | 34143 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-11 | 45393.3542 | 2024-04-11 | 45393.6521 | 0.15214 | 0.00035463 | 222 | 95238 | Planned | Planned
121 |  | 34144 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-04-11 | 45393.3486 | 2024-04-11 | 45393.3792 | 0.00064218 | 1.5976e-05 | 10 | 402 | Planned | Planned
122 |  | 34146 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-11 | 45393.3542 | 2024-04-11 | 45393.6639 | 0.0014249 | 3.194e-06 | 2 | 892 | Planned | Planned
123 |  | 34147 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-11 | 45393.3757 | 2024-04-11 | 45393.7153 | 0.083584 | 0.00017093 | 107 | 52323 | Planned | Planned
124 |  | 34149 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-04-11 | 45393.375 | 2024-04-11 | 45393.4979 | 0.053723 | 0.00030352 | 190 | 33630 | Planned | Planned
125 |  | 34150 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | MKAU K07 | 2024-04-11 | 45393.4215 | 2024-04-11 | 45393.6708 | 0.011278 | 0.0028195 | 1765 | 7060 | Unplanned | Vegetation
126 |  | 34150 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | TAKA K12 | 2024-04-11 | 45393.4215 | 2024-04-11 | 45393.6708 | 0.095603 | 0.0015463 | 968 | 59847 | Unplanned | Vegetation
127 |  | 34151 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-04-11 | 45393.4167 | 2024-04-11 | 45393.6576 | 0.10421 | 0.00030032 | 188 | 65236 | Planned | Planned
128 |  | 34152 | BALM K04 - K04 TRURO ROAD | Auckland | BALM K04 | 2024-04-11 | 45393.4521 | 2024-04-11 | 45393.6764 | 0.25837 | 0.0024026 | 1504 | 161738 | Unplanned | Defective equipment
129 |  | 34153 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-04-11 | 45393.4028 | 2024-04-11 | 45393.6354 | 0.011773 | 3.5143e-05 | 22 | 7370 | Planned | Planned
130 |  | 34154 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-11 | 45393.5493 | 2024-04-11 | 45393.65 | 0.022601 | 0.0001933 | 121 | 14148 | Unplanned | Vegetation
131 |  | 34155 | AVON K01 - K01 BLOCKHOUSE BAY RD.(353) | Auckland | AVON K01 | 2024-04-11 | 45393.5722 | 2024-04-11 | 45393.7458 | 0.27121 | 0.0032077 | 2008 | 169776 | Unplanned | Defective equipment
132 |  | 34156 | RIVE K04 - K04 BARRETT RD | Northern | RIVE K04 | 2024-04-11 | 45393.5854 | 2024-04-11 | 45393.8868 | 0.43004 | 0.0018802 | 1177 | 269203 | Unplanned | Vegetation
133 |  | 34157 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-04-11 | 45393.5938 | 2024-04-12 | 45394.6681 | 0.20109 | 0.0025927 | 1221 | 125881 | Unplanned | Defective equipment
134 |  | 34158 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-04-11 | 45393.6083 | 2024-04-11 | 45393.6868 | 0.045128 | 0.00039936 | 250 | 28250 | Unplanned | Vegetation
135 |  | 34159 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2024-04-11 | 45393.6069 | 2024-04-11 | 45393.75 | 0.015441 | 0.00085783 | 537 | 9666 | Unplanned | Defective equipment
136 |  | 34159 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K06 | 2024-04-11 | 45393.6069 | 2024-04-11 | 45393.75 | 0.088688 | 0.00063739 | 399 | 55518 | Unplanned | Defective equipment
137 |  | 34160 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-11 | 45393.6062 | 2024-04-11 | 45393.9736 | 0.069045 | 0.0017203 | 1077 | 43222 | Unplanned | Defective equipment
138 |  | 34161 | BMON K04 - K04 GRAMMAR SCHOOL + LS | Northern | BMON K04 | 2024-04-11 | 45393.6312 | 2024-04-11 | 45393.85 | 0.2374 | 0.00080193 | 502 | 148614 | Unplanned | Defective equipment
139 |  | 34162 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-04-11 | 45393.5938 | 2024-04-11 | 45393.6674 | 0.048508 | 0.00062936 | 394 | 30366 | Unplanned | Cause unknown
140 |  | 34163 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2024-04-11 | 45393.6694 | 2024-04-11 | 45393.6986 | 0.03462 | 0.00082429 | 516 | 21672 | Unplanned | Vegetation
141 |  | 34164 | HOBV K11 - K11 TRIG RD +LS | Northern | HOBV K11 | 2024-04-11 | 45393.5813 | 2024-04-11 | 45393.6458 | 0.0016342 | 1.7571e-05 | 11 | 1023 | Unplanned | Cause unknown
142 |  | 34165 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-04-11 | 45393.6687 | 2024-04-11 | 45393.7833 | 0.11969 | 0.001393 | 872 | 74926 | Unplanned | Cause unknown
143 |  | 34165 | RANU K04 - K04 GLEN ROAD | Northern | TRIA K10 | 2024-04-11 | 45393.6687 | 2024-04-11 | 45393.7833 | 0.12776 | 0.0013738 | 860 | 79980 | Unplanned | Cause unknown
144 |  | 34166 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-04-11 | 45393.5854 | 2024-04-11 | 45393.6875 | 0.0032876 | 2.2363e-05 | 14 | 2058 | Unplanned | Vegetation
145 |  | 34167 | PONS K12 - K12 RICHMOND ROAD | Auckland | PONS K12 | 2024-04-11 | 45393.7681 | 2024-04-12 | 45394.1715 | 0.20651 | 0.00097285 | 609 | 129274 | Unplanned | Third party interference
146 |  | 34168 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-04-11 | 45393.8 | 2024-04-12 | 45394.3958 | 0.058304 | 0.00032748 | 205 | 36498 | Unplanned | Adverse weather | 1. Event is classified as Major Event under DPP3 determination 2. Windspeed was greater than 55 km/h within 6 hours of the event start time 3. The asset affected is susceptible to wind damage
147 |  | 34169 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-11 | 45393.559 | 2024-04-11 | 45393.6528 | 0.0094889 | 7.0283e-05 | 44 | 5940 | Unplanned | Cause unknown
148 |  | 34170 | NSBT46 - NEW LYNN P276 - BRICKWORKS K06 (46) | Northern | BRIC K03 | 2024-04-11 | 45393.8167 | 2024-04-11 | 45393.9257 | 0.031524 | 0.00080833 | 506 | 19734 | Unplanned | Defective equipment
149 |  | 34170 | NSBT46 - NEW LYNN P276 - BRICKWORKS K06 (46) | Northern | BRIC K04 | 2024-04-11 | 45393.8167 | 2024-04-11 | 45393.9257 | 0.10789 | 0.0017828 | 1116 | 67536 | Unplanned | Defective equipment
150 |  | 34170 | NSBT46 - NEW LYNN P276 - BRICKWORKS K06 (46) | Northern | BRIC K05 | 2024-04-11 | 45393.8167 | 2024-04-11 | 45393.9257 | 0.0028275 | 0.00028276 | 177 | 1770 | Unplanned | Defective equipment
151 |  | 34170 | NSBT46 - NEW LYNN P276 - BRICKWORKS K06 (46) | Northern | BRIC K09 | 2024-04-11 | 45393.8167 | 2024-04-11 | 45393.9257 | 0.0017556 | 0.0002508 | 157 | 1099 | Unplanned | Defective equipment
152 |  | 34170 | NSBT46 - NEW LYNN P276 - BRICKWORKS K06 (46) | Northern | BRIC K10 | 2024-04-11 | 45393.8167 | 2024-04-11 | 45393.9257 | 0.032371 | 0.0019042 | 1192 | 20264 | Unplanned | Defective equipment
153 |  | 34170 | NSBT46 - NEW LYNN P276 - BRICKWORKS K06 (46) | Northern | NLYN K04 | 2024-04-11 | 45393.8167 | 2024-04-11 | 45393.9257 | 0.011786 | 0.0016837 | 1054 | 7378 | Unplanned | Defective equipment
154 |  | 34175 | RDAL K12 - K12 JACK HINTON DR | Northern | RDAL K12 | 2024-04-11 | 45393.9208 | 2024-04-12 | 45394.05 | 0.013074 | 7.0288e-05 | 44 | 8184 | Planned | Planned
155 |  | 34176 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-04-11 | 45393.8187 | 2024-04-11 | 45393.9271 | 0.038876 | 0.00024921 | 156 | 24336 | Unplanned | Defective equipment
156 |  | 34177 | SYLV K16 - K16 31 CARBINE RD | Auckland | SYLV K16 | 2024-04-11 | 45393.9444 | 2024-04-12 | 45394.2042 | 0.0035847 | 9.584e-06 | 6 | 2244 | Planned | Planned
157 |  | 34180 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-04-11 | 45393.6451 | 2024-04-11 | 45393.8361 | 0.008786 | 3.1948e-05 | 20 | 5500 | Unplanned | Vegetation
158 |  | 34183 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K03 | 2024-04-11 | 45393.9792 | 2024-04-12 | 45394.1382 | 0.038449 | 0.00018051 | 113 | 24069 | Planned | Planned
159 |  | 34183 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K07 | 2024-04-11 | 45393.9792 | 2024-04-12 | 45394.1382 | 0.018291 | 7.9872e-05 | 50 | 11450 | Planned | Planned
160 |  | 34185 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-04-12 | 45394 | 2024-04-12 | 45394.0021 | 0.0018403 | 0.00061341 | 384 | 1152 | Unplanned | Vegetation
161 |  | 34186 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-11 | 45393.7993 | 2024-04-11 | 45393.9194 | 0.00304 | 1.7572e-05 | 11 | 1903 | Unplanned | Defective equipment
162 |  | 34189 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-11 | 45393.7792 | 2024-04-12 | 45394.0236 | 0.0044984 | 1.2777e-05 | 8 | 2816 | Unplanned | Defective equipment
163 |  | 34190 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-04-11 | 45393.591 | 2024-04-12 | 45394.0417 | 0.011404 | 1.7572e-05 | 11 | 7139 | Unplanned | Cause unknown
164 |  | 34191 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-04-11 | 45393.6076 | 2024-04-12 | 45394.1146 | 0.023323 | 3.1949e-05 | 20 | 14600 | Unplanned | Vegetation
165 |  | 34192 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-04-12 | 45394.1111 | 2024-04-12 | 45394.7 | 0.23708 | 0.00091215 | 571 | 148408 | Unplanned | Defective equipment
166 |  | 34195 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-04-12 | 45394.1167 | 2024-04-12 | 45394.4111 | 0.045381 | 0.00010703 | 67 | 28408 | Unplanned | Defective equipment
167 |  | 34196 | GHIT K04 - K04 KYLE RD | Northern | GHIT K04 | 2024-04-12 | 45394.1542 | 2024-04-12 | 45394.1826 | 0.062881 | 0.0024457 | 1531 | 39363 | Unplanned | Human error
168 |  | 34197 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-04-11 | 45393.7292 | 2024-04-12 | 45394.1951 | 0.0010719 | 1.597e-06 | 1 | 671 | Unplanned | Defective equipment
169 |  | 34198 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2024-04-12 | 45394.1743 | 2024-04-12 | 45394.2257 | 0.055306 | 0.0014601 | 914 | 34621 | Unplanned | Defective equipment
170 |  | 34199 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2024-04-11 | 45393.9799 | 2024-04-12 | 45394.1813 | 0.012508 | 4.3131e-05 | 27 | 7830 | Planned | Planned
171 |  | 34201 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | MKAU K07 | 2024-04-12 | 45394.2069 | 2024-04-12 | 45394.7708 | 0.0028435 | 0.0028435 | 1780 | 1780 | Unplanned | Human error
172 |  | 34201 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | TAKA K12 | 2024-04-12 | 45394.2069 | 2024-04-12 | 45394.7708 | 0.11855 | 0.0015463 | 968 | 74209 | Unplanned | Human error
173 |  | 34203 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2024-04-12 | 45394.1049 | 2024-04-12 | 45394.3125 | 0.031524 | 0.00010543 | 66 | 19734 | Unplanned | Vegetation
174 |  | 34204 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-12 | 45394.3042 | 2024-04-12 | 45394.5903 | 0.019086 | 4.6326e-05 | 29 | 11948 | Unplanned | Defective equipment
175 |  | 34205 | MANL K07 - K07 LAURENCE ST | Northern | MANL K07 | 2024-04-12 | 45394.3264 | 2024-04-12 | 45394.6326 | 0.095105 | 0.00021566 | 135 | 59535 | Unplanned | Defective equipment
176 |  | 34206 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-04-12 | 45394.3333 | 2024-04-12 | 45394.6625 | 0.040889 | 8.626e-05 | 54 | 25596 | Planned | Planned
177 |  | 34208 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-04-12 | 45394.2736 | 2024-04-12 | 45394.3819 | 0.0002492 | 1.597e-06 | 1 | 156 | Unplanned | Adverse weather | 1. Event is classified as Major Event under DPP3 determination 2. Windspeed was greater than 55 km/h within 6 hours of the event start time 3. The asset affected is susceptible to wind damage
178 |  | 34209 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-04-12 | 45394.4688 | 2024-04-12 | 45394.7035 | 0.071403 | 0.0017428 | 1091 | 44698 | Unplanned | Third party interference
179 |  | 34210 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-04-12 | 45394.2312 | 2024-04-12 | 45394.8646 | 0.075758 | 8.3069e-05 | 52 | 47424 | Unplanned | Human error
180 |  | 34210 | MANU K12 - K12 ALFRISTON RD | Auckland | TAKA K12 | 2024-04-12 | 45394.2312 | 2024-04-12 | 45394.8646 | 0.0025911 | 3.9935e-05 | 25 | 1622 | Unplanned | Human error
181 |  | 34211 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-04-12 | 45394.4688 | 2024-04-12 | 45394.6931 | 0.0015479 | 4.792e-06 | 3 | 969 | Unplanned | Defective equipment
182 |  | 34212 | RIVE K11 - K11 CARTERS MILL | Northern | RIVE K11 | 2024-04-11 | 45393.8826 | 2024-04-12 | 45394.4965 | 0.0014122 | 1.597e-06 | 1 | 884 | Unplanned | Adverse weather | 1. Event is classified as Major Event under DPP3 determination 2. Windspeed was greater than 55 km/h within 6 hours of the event start time 3. The asset affected is susceptible to wind damage
183 |  | 34213 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-12 | 45394.4549 | 2024-04-12 | 45394.5875 | 0.0033563 | 1.7572e-05 | 11 | 2101 | Unplanned | Defective equipment
184 |  | 34214 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-04-12 | 45394.2882 | 2024-04-12 | 45394.4549 | 0.0099681 | 4.1534e-05 | 26 | 6240 | Unplanned | Human error
185 |  | 34215 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-04-12 | 45394.2375 | 2024-04-12 | 45394.7389 | 0.016147 | 2.2364e-05 | 14 | 10108 | Unplanned | Human error
186 |  | 34217 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-12 | 45394.4215 | 2024-04-12 | 45394.5514 | 0.0013786 | 7.983e-06 | 5 | 863 | Planned | Planned
187 |  | 34218 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-04-12 | 45394.2472 | 2024-04-12 | 45394.4722 | 0.00051758 | 1.597e-06 | 1 | 324 | Unplanned | Defective equipment
188 |  | 34219 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-04-12 | 45394.4535 | 2024-04-12 | 45394.5396 | 0.015054 | 0.00012141 | 76 | 9424 | Unplanned | Adverse weather | 1. Event is classified as Major Event under DPP3 determination 2. Windspeed was greater than 55 km/h within 6 hours of the event start time 3. The asset affected is susceptible to wind damage
189 |  | 34220 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-04-12 | 45394.3743 | 2024-04-12 | 45394.5764 | 0.00046486 | 1.597e-06 | 1 | 291 | Unplanned | Defective equipment
190 |  | 34221 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-04-12 | 45394.4347 | 2024-04-12 | 45394.6104 | 0.00040416 | 1.597e-06 | 1 | 253 | Unplanned | Human error
191 |  | 34222 | PAPA K06 - K06 13 PORCHESTER RD | Auckland | PAPA K06 | 2024-04-12 | 45394.4618 | 2024-04-12 | 45394.9938 | 0.069748 | 9.1055e-05 | 57 | 43662 | Unplanned | Vegetation
192 |  | 34224 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-04-12 | 45394.7639 | 2024-04-12 | 45394.9722 | 0.011412 | 0.0014265 | 893 | 7144 | Unplanned | Vegetation
193 |  | 34224 | COAT K03 - K03 SCREEN ROAD | Northern | MKIN K11 | 2024-04-12 | 45394.7639 | 2024-04-12 | 45394.9722 | 0.35272 | 0.0011757 | 736 | 220800 | Unplanned | Vegetation
194 |  | 34224 | COAT K03 - K03 SCREEN ROAD | Northern | SPUR K02 | 2024-04-12 | 45394.7639 | 2024-04-12 | 45394.9722 | 0.13862 | 0.0017461 | 1093 | 86778 | Unplanned | Vegetation
195 |  | 34225 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-12 | 45394.3757 | 2024-04-12 | 45394.6861 | 0.076405 | 0.00017093 | 107 | 47829 | Planned | Planned
196 |  | 34226 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-04-12 | 45394.8 | 2024-04-12 | 45394.8194 | 0.00017892 | 6.39e-06 | 4 | 112 | Unplanned | Vegetation
197 |  | 34227 | HVAL K02 - K02 CORBAN AVENUE | Northern | HVAL K02 | 2024-04-12 | 45394.75 | 2024-04-12 | 45394.7882 | 0.0021965 | 3.9936e-05 | 25 | 1375 | Planned | Planned
198 |  | 34229 | SHOW K05 - K05 LITTEN RD | Auckland | SHOW K05 | 2024-04-13 | 45395 | 2024-04-13 | 45395.1438 | 0.094902 | 0.00048563 | 304 | 59408 | Planned | Planned
199 |  | 34230 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-13 | 45395.375 | 2024-04-13 | 45395.7028 | 0.085202 | 0.0001805 | 113 | 53336 | Planned | Planned
200 |  | 34231 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-04-13 | 45395.375 | 2024-04-13 | 45395.6493 | 0.008834 | 2.2364e-05 | 14 | 5530 | Planned | Planned
201 |  | 34232 | KING K09 - K09 381 NEW NORTH RD | Auckland | KING K09 | 2024-04-13 | 45395.375 | 2024-04-13 | 45395.7701 | 0.1418 | 0.0002492 | 156 | 88764 | Planned | Planned
202 |  | 34235 | HVAL K06 - K06 CATHERINE ST | Northern | HVAL K06 | 2024-04-12 | 45394.6181 | 2024-04-13 | 45395.8938 | 0.0029345 | 1.597e-06 | 1 | 1837 | Unplanned | Defective equipment
203 |  | 34236 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-04-13 | 45395.4965 | 2024-04-13 | 45395.7021 | 0.10555 | 0.0010655 | 571 | 66074 | Unplanned | Vegetation
204 |  | 34238 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-04-13 | 45395.5188 | 2024-04-13 | 45395.691 | 0.0055464 | 2.2364e-05 | 14 | 3472 | Unplanned | Defective equipment
205 |  | 34240 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-04-13 | 45395.4396 | 2024-04-13 | 45395.6146 | 0.084135 | 0.00033387 | 209 | 52668 | Planned | Planned
206 |  | 34241 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-04-13 | 45395.7167 | 2024-04-13 | 45395.75 | 0.00048882 | 1.5975e-05 | 10 | 306 | Planned | Planned
207 |  | 34242 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-04-11 | 45393.5785 | 2024-04-11 | 45393.6458 | 0.017355 | 0.00017892 | 112 | 10864 | Unplanned | Vegetation
208 |  | 34243 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-04-13 | 45395.8125 | 2024-04-13 | 45395.8785 | 0.00045528 | 4.792e-06 | 3 | 285 | Unplanned | Defective equipment
209 |  | 34244 | RIVE K11 - K11 CARTERS MILL | Northern | RIVE K11 | 2024-04-11 | 45393.466 | 2024-04-11 | 45393.5556 | 0.00020607 | 1.597e-06 | 1 | 129 | Unplanned | Vegetation
210 |  | 34245 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-04-14 | 45396.0667 | 2024-04-14 | 45396.1514 | 0.091079 | 0.0046086 | 1778 | 57015 | Unplanned | Vegetation
211 |  | 34246 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-14 | 45396.1319 | 2024-04-14 | 45396.5549 | 0.058699 | 0.00070761 | 443 | 36745 | Unplanned | Defective equipment
212 |  | 34247 | SYLV K15 - K15 25 CARBINE RD SW STN | Auckland | SYLV K15 | 2024-04-14 | 45396.3688 | 2024-04-14 | 45396.4264 | 0.00013259 | 1.597e-06 | 1 | 83 | Planned | Planned
213 |  | 34248 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-04-13 | 45395.375 | 2024-04-13 | 45395.6201 | 0.0016917 | 4.792e-06 | 3 | 1059 | Planned | Planned
214 |  | 34249 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-04-14 | 45396.4924 | 2024-04-14 | 45396.6646 | 0.044371 | 0.0001789 | 112 | 27776 | Unplanned | Vegetation
215 |  | 34252 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-04-14 | 45396.7708 | 2024-04-14 | 45396.9028 | 0.00091055 | 4.792e-06 | 3 | 570 | Unplanned | Cause unknown
216 |  | 34253 | NEWM K10 - K10 SMITH EQUITY | Auckland | NEWM K10 | 2024-04-14 | 45396.9583 | 2024-04-15 | 45397.0444 | 0.00931 | 7.5081e-05 | 47 | 5828 | Planned | Planned
217 |  | 34254 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-14 | 45396.9535 | 2024-04-15 | 45397.0111 | 0.0064969 | 7.8273e-05 | 49 | 4067 | Unplanned | Defective equipment
218 |  | 34255 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-14 | 45396.9792 | 2024-04-15 | 45397.191 | 0.0092573 | 3.0352e-05 | 19 | 5795 | Planned | Planned
219 |  | 34256 | FREE K19 - K19 131 WELLINGTON ST | Auckland | FREE K64 | 2024-04-14 | 45396.9313 | 2024-04-15 | 45397.1271 | 0.01892 | 6.7093e-05 | 42 | 11844 | Planned | Planned
220 |  | 34257 | ORAK K04 - K04 HAWERA RD | Auckland | ORAK K04 | 2024-04-15 | 45397.0833 | 2024-04-15 | 45397.1687 | 0.00019649 | 1.597e-06 | 1 | 123 | Planned | Planned
221 |  | 34258 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-15 | 45397.1292 | 2024-04-15 | 45397.1583 | 0.039039 | 0.0015144 | 948 | 24438 | Unplanned | Defective equipment
222 |  | 34259 | HOBV K11 - K11 TRIG RD +LS | Northern | HOBV K11 | 2024-04-15 | 45397.1646 | 2024-04-15 | 45397.2278 | 0.0017444 | 1.9168e-05 | 12 | 1092 | Unplanned | Defective equipment
223 |  | 34260 | SUNS K10 - K10 MATTHEWS ROAD + LS | Northern | SUNS K10 | 2024-04-15 | 45397.25 | 2024-04-15 | 45397.3111 | 0.0082189 | 9.5847e-05 | 60 | 5145 | Planned | Planned
224 |  | 34261 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-04-15 | 45397.2604 | 2024-04-15 | 45397.3715 | 0.001278 | 7.987e-06 | 5 | 800 | Unplanned | Cause unknown
225 |  | 34262 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-04-15 | 45397.375 | 2024-04-15 | 45397.6076 | 0.00053515 | 1.597e-06 | 1 | 335 | Planned | Planned
226 |  | 34263 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-04-15 | 45397.4014 | 2024-04-15 | 45397.709 | 0.023353 | 5.2716e-05 | 33 | 14619 | Planned | Planned
227 |  | 34264 | MCEN K05 - K05 BADER DRIVE | Auckland | MCEN K05 | 2024-04-15 | 45397.3958 | 2024-04-15 | 45397.5903 | 0.032205 | 0.00011502 | 72 | 20160 | Planned | Planned
228 |  | 34265 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-04-15 | 45397.3986 | 2024-04-15 | 45397.7146 | 0.11557 | 0.00025399 | 159 | 72345 | Planned | Planned
229 |  | 34266 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-04-15 | 45397.3958 | 2024-04-15 | 45397.691 | 0.0040735 | 9.585e-06 | 6 | 2550 | Planned | Planned
230 |  | 34267 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-04-15 | 45397.4236 | 2024-04-15 | 45397.5903 | 0.0015336 | 6.389e-06 | 4 | 960 | Planned | Planned
231 |  | 34268 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-15 | 45397.4028 | 2024-04-15 | 45397.6285 | 0.029593 | 9.1052e-05 | 57 | 18525 | Planned | Planned
232 |  | 34269 | NSBT5 - WAIRAU VALLEY H28 - T1 MILFORD K05 (5) | Northern | MILF K01 | 2024-04-15 | 45397.6618 | 2024-04-15 | 45397.6847 | 0.0021406 | 0.00053515 | 335 | 1340 | Unplanned | Wildlife
233 |  | 34269 | NSBT5 - WAIRAU VALLEY H28 - T1 MILFORD K05 (5) | Northern | MILF K02 | 2024-04-15 | 45397.6618 | 2024-04-15 | 45397.6847 | 0.011134 | 0.0011134 | 697 | 6970 | Unplanned | Wildlife
234 |  | 34269 | NSBT5 - WAIRAU VALLEY H28 - T1 MILFORD K05 (5) | Northern | MILF K03 | 2024-04-15 | 45397.6618 | 2024-04-15 | 45397.6847 | 0.027783 | 0.0017364 | 1087 | 17392 | Unplanned | Wildlife
235 |  | 34269 | NSBT5 - WAIRAU VALLEY H28 - T1 MILFORD K05 (5) | Northern | MILF K04 | 2024-04-15 | 45397.6618 | 2024-04-15 | 45397.6847 | 0.0062509 | 0.00048084 | 301 | 3913 | Unplanned | Wildlife
236 |  | 34269 | NSBT5 - WAIRAU VALLEY H28 - T1 MILFORD K05 (5) | Northern | MILF K06 | 2024-04-15 | 45397.6618 | 2024-04-15 | 45397.6847 | 0.004385 | 0.00087701 | 549 | 2745 | Unplanned | Wildlife
237 |  | 34270 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-15 | 45397.6854 | 2024-04-15 | 45397.7118 | 0.00030352 | 7.987e-06 | 5 | 190 | Unplanned | Defective equipment
238 |  | 34271 | TAKA K09 - K09 TAKA ST | Auckland | TAKA K09 | 2024-04-15 | 45397.9167 | 2024-04-16 | 45398.0847 | 0.032087 | 0.00013259 | 83 | 20086 | Planned | Planned
239 |  | 34272 | ROCK K09 - K09 604 GREAT SOUTH RD | Auckland | ROCK K09 | 2024-04-15 | 45397.9583 | 2024-04-16 | 45398.0417 | 0.0053675 | 4.4729e-05 | 28 | 3360 | Planned | Planned
240 |  | 34274 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-04-15 | 45397.95 | 2024-04-15 | 45397.9951 | 0.015783 | 0.00024281 | 152 | 9880 | Unplanned | Third party interference
241 |  | 34275 | HAUR K02 - K02 LAKE ROAD | Northern | HAUR K02 | 2024-04-16 | 45398.3542 | 2024-04-16 | 45398.6479 | 0.058112 | 0.00013738 | 86 | 36378 | Planned | Planned
242 |  | 34276 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-04-16 | 45398.375 | 2024-04-16 | 45398.659 | 0.068603 | 0.00016773 | 105 | 42945 | Planned | Planned
243 |  | 34277 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-04-16 | 45398.3542 | 2024-04-16 | 45398.7236 | 0.20226 | 0.0003802 | 238 | 126616 | Planned | Planned
244 |  | 34278 | WSWA K03 - K03 MARSHALL LAING ST | Auckland | WSWA K03 | 2024-04-16 | 45398.4167 | 2024-04-16 | 45398.6493 | 0.07171 | 0.00021406 | 134 | 44890 | Planned | Planned
245 |  | 34280 | SHEL K06 - K06 RIDDELL RD EAST | Auckland | SHEL K06 | 2024-04-16 | 45398.4396 | 2024-04-16 | 45398.6146 | 0.00040256 | 1.597e-06 | 1 | 252 | Unplanned | Third party interference
246 |  | 34281 | KING K06 - K06 CENTRAL RD | Auckland | KING K06 | 2024-04-16 | 45398.6104 | 2024-04-16 | 45398.7604 | 0.13097 | 0.0014026 | 878 | 81986 | Unplanned | Defective equipment
247 |  | 34282 | ROSE K01 - K01 GLUCINA SMELTERS | Auckland | ROSE K01 | 2024-04-17 | 45399.0833 | 2024-04-17 | 45399.1646 | 0.0013083 | 1.1182e-05 | 7 | 819 | Planned | Planned
248 |  | 34283 | NLYN K01 - K01 ARAWA ST | Northern | NLYN K01 | 2024-04-17 | 45399.3549 | 2024-04-17 | 45399.6819 | 0.2513 | 0.00053355 | 334 | 157314 | Planned | Planned
249 |  | 34284 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-04-17 | 45399.3438 | 2024-04-17 | 45399.6778 | 0.030154 | 6.39e-05 | 40 | 18876 | Planned | Planned
250 |  | 34285 | BIRK K12 - K12 STANLEY ROAD | Northern | BIRK K12 | 2024-04-17 | 45399.375 | 2024-04-17 | 45399.6243 | 0.10437 | 0.00029074 | 182 | 65338 | Planned | Planned
251 |  | 34286 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-17 | 45399.3771 | 2024-04-17 | 45399.691 | 0.010109 | 2.2364e-05 | 14 | 6328 | Planned | Planned
252 |  | 34287 | MKIN K02 - K02 TAWA DRIVE | Northern | MKIN K02 | 2024-04-17 | 45399.3958 | 2024-04-17 | 45399.5944 | 0.00091375 | 3.195e-06 | 2 | 572 | Planned | Planned
253 |  | 34288 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-04-17 | 45399.3785 | 2024-04-17 | 45399.3903 | 2.7157e-05 | 1.597e-06 | 1 | 17 | Unplanned | Other Cause | Outage caused by Tap Operation
254 |  | 34289 | WSWA K06 - K06 ROSKILL RIPPLE | Auckland | WSWA K06 | 2024-04-17 | 45399.4556 | 2024-04-17 | 45399.6035 | 0.022117 | 0.00010383 | 65 | 13845 | Planned | Planned
255 |  | 34290 | WIRI K21 - K21 WIRI INDUSTRIAL PARK No.2 | Auckland | WIRI K21 | 2024-04-17 | 45399.5687 | 2024-04-17 | 45399.625 | 0.00038818 | 4.792e-06 | 3 | 243 | Unplanned | Third party interference
256 |  | 34291 | WIRI K18 - K18 ASH RD | Auckland | WIRI K18 | 2024-04-17 | 45399.7299 | 2024-04-17 | 45399.8021 | 0.00033227 | 3.195e-06 | 2 | 208 | Planned | Planned
257 |  | 34292 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-04-17 | 45399.6799 | 2024-04-17 | 45399.7632 | 0.0013419 | 1.1182e-05 | 7 | 840 | Unplanned | Vegetation
258 |  | 34293 | ECOA K02 - K02 SUNRISE AVENUE | Northern | ECOA K02 | 2024-04-18 | 45400.3347 | 2024-04-18 | 45400.7056 | 0.21923 | 0.00041055 | 257 | 137238 | Planned | Planned
259 |  | 34294 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-04-18 | 45400.3542 | 2024-04-18 | 45400.7007 | 0.029494 | 5.9106e-05 | 37 | 18463 | Planned | Planned
260 |  | 34295 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-04-18 | 45400.375 | 2024-04-18 | 45400.5556 | 0.0037381 | 1.4377e-05 | 9 | 2340 | Planned | Planned
261 |  | 34296 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-04-18 | 45400.3771 | 2024-04-18 | 45400.6188 | 0.0016677 | 4.792e-06 | 3 | 1044 | Planned | Planned
262 |  | 34297 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-04-18 | 45400.3799 | 2024-04-18 | 45400.6417 | 0.037941 | 0.00010064 | 63 | 23751 | Planned | Planned
263 |  | 34298 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-04-18 | 45400.3889 | 2024-04-18 | 45400.6771 | 0.0026518 | 6.39e-06 | 4 | 1660 | Planned | Planned
264 |  | 34299 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-04-18 | 45400.5729 | 2024-04-18 | 45400.6458 | 0.00067093 | 6.39e-06 | 4 | 420 | Unplanned | Third party interference
265 |  | 34300 | KEEL K10 - K10 HUHTAMAKI | Northern | KEEL K10 | 2024-04-18 | 45400.8333 | 2024-04-18 | 45400.9646 | 0.00030192 | 1.597e-06 | 1 | 189 | Planned | Planned
266 |  | 34301 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-04-18 | 45400.9792 | 2024-04-19 | 45401.3333 | 0.09525 | 0.00029234 | 183 | 59626 | Planned | Planned
267 |  | 34302 | BALM K05 - K05 BRIXTON ROAD | Auckland | BALM K05 | 2024-04-18 | 45400.9799 | 2024-04-19 | 45401.1951 | 0.093995 | 0.00033706 | 211 | 58840 | Planned | Planned
268 |  | 34303 | RBEA K03 - K03 BAY ST | Northern | RBEA K03 | 2024-04-19 | 45401.0569 | 2024-04-19 | 45401.1111 | 0.0001246 | 1.597e-06 | 1 | 78 | Unplanned | Defective equipment
269 |  | 34306 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-04-19 | 45401.3333 | 2024-04-19 | 45401.6687 | 0.095675 | 0.00019808 | 124 | 59892 | Planned | Planned
270 |  | 34307 | HPOI K06 - K06 WISELEY RD | Northern | HPOI K06 | 2024-04-19 | 45401.3458 | 2024-04-19 | 45401.509 | 0.00017892 | 6.39e-06 | 2 | 112 | Planned | Planned
271 |  | 34308 | PAPA K13 - K13 BATES ST | Auckland | PAPA K13 | 2024-04-19 | 45401.3764 | 2024-04-19 | 45401.6528 | 0.1119 | 0.00028115 | 176 | 70048 | Planned | Planned
272 |  | 34309 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-04-19 | 45401.2819 | 2024-04-19 | 45401.3729 | 0.00083707 | 6.389e-06 | 4 | 524 | Unplanned | Cause unknown
273 |  | 34310 | BAIR K14 - K14 WYMONDLEY | Auckland | BAIR K14 | 2024-04-19 | 45401.4125 | 2024-04-19 | 45401.5028 | 0.045272 | 0.00034825 | 218 | 28340 | Planned | Planned
274 |  | 34311 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-04-19 | 45401.3979 | 2024-04-19 | 45401.6028 | 0.00047125 | 1.597e-06 | 1 | 295 | Planned | Planned
275 |  | 34312 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-19 | 45401.6625 | 2024-04-20 | 45402.4972 | 0.015221 | 0.0006805 | 426 | 9528 | Unplanned | Defective equipment
276 |  | 34313 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-04-19 | 45401.5806 | 2024-04-20 | 45402.0444 | 0.061397 | 0.00017572 | 110 | 38434 | Unplanned | Vegetation
277 |  | 34314 | SUNS K10 - K10 MATTHEWS ROAD + LS | Northern | SUNS K10 | 2024-04-19 | 45401.7292 | 2024-04-19 | 45401.7604 | 0.0040496 | 9.5848e-05 | 60 | 2535 | Planned | Planned
278 |  | 34315 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-19 | 45401.9174 | 2024-04-20 | 45402.1687 | 0.067659 | 0.0001869 | 117 | 42354 | Planned | Planned
279 |  | 34316 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-04-20 | 45402.3542 | 2024-04-20 | 45402.7819 | 0.20173 | 0.00032748 | 205 | 126280 | Planned | Planned
280 |  | 34317 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-04-20 | 45402.3361 | 2024-04-20 | 45402.7785 | 0.011193 | 1.7572e-05 | 11 | 7007 | Planned | Planned
281 |  | 34318 | MLEO K05 - K05 CARHAVEN | Northern | MLEO K05 | 2024-04-20 | 45402.3542 | 2024-04-20 | 45402.4861 | 0.00030352 | 1.597e-06 | 1 | 190 | Planned | Planned
282 |  | 34319 | DRIV K13 - K13 KING EDWARD AVE | Auckland | DRIV K13 | 2024-04-20 | 45402.375 | 2024-04-20 | 45402.7049 | 0.11078 | 0.00023323 | 146 | 69350 | Planned | Planned
283 |  | 34322 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-04-20 | 45402.3285 | 2024-04-20 | 45402.4062 | 0.00017892 | 1.597e-06 | 1 | 112 | Unplanned | Cause unknown
284 |  | 34323 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-04-20 | 45402.4167 | 2024-04-20 | 45402.6319 | 0.013866 | 4.4729e-05 | 28 | 8680 | Planned | Planned
285 |  | 34324 | OREW K10 - K10 HATFIELDS | Northern | OREW K10 | 2024-04-20 | 45402.375 | 2024-04-20 | 45402.6111 | 0.00054314 | 1.597e-06 | 1 | 340 | Planned | Planned
286 |  | 34325 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2024-04-20 | 45402.375 | 2024-04-20 | 45402.6667 | 0.022812 | 5.4314e-05 | 34 | 14280 | Planned | Planned
287 |  | 34326 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-04-20 | 45402.375 | 2024-04-20 | 45402.7306 | 0.052346 | 0.00010224 | 64 | 32768 | Planned | Planned
288 |  | 34327 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-04-20 | 45402.3799 | 2024-04-20 | 45402.6569 | 0.037606 | 9.425e-05 | 59 | 23541 | Planned | Planned
289 |  | 34328 | HCRE K02 - K02 FOWLER STREET | Northern | HCRE K02 | 2024-04-20 | 45402.4965 | 2024-04-20 | 45402.55 | 0.0020911 | 2.7157e-05 | 17 | 1309 | Unplanned | Cause unknown
290 |  | 34329 | MKAU K27 - K27 CARTER HOLT (VIA LST1) | Auckland | MKAU K27 | 2024-04-20 | 45402.5229 | 2024-04-20 | 45402.7569 | 0.38747 | 0.0026837 | 1680 | 242552 | Unplanned | Third party interference
291 |  | 34330 | TRIA K02 - K02 SOUTH | Northern | TRIA K02 | 2024-04-20 | 45402.6667 | 2024-04-20 | 45402.6806 | 9.5848e-05 | 4.792e-06 | 3 | 60 | Unplanned | Other Cause | Outage caused by Tap Operation
292 |  | 34331 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-04-20 | 45402.6215 | 2024-04-20 | 45402.7514 | 0.0029872 | 1.5974e-05 | 10 | 1870 | Unplanned | Vegetation
293 |  | 34332 | NSBT57 - WARKWORTH P280 - SANDSPIT H04 (57) | Northern | SNEL K07 | 2024-04-21 | 45403.1062 | 2024-04-21 | 45403.6875 | 0.076823 | 0.0032828 | 2055 | 48091 | Unplanned | Third party interference
294 |  | 34332 | NSBT57 - WARKWORTH P280 - SANDSPIT H04 (57) | Northern | SNEL K08 | 2024-04-21 | 45403.1062 | 2024-04-21 | 45403.6875 | 0.004639 | 0.0011598 | 726 | 2904 | Unplanned | Third party interference
295 |  | 34332 | NSBT57 - WARKWORTH P280 - SANDSPIT H04 (57) | Northern | SNEL K10 | 2024-04-21 | 45403.1062 | 2024-04-21 | 45403.6875 | 0.0043259 | 0.0010816 | 677 | 2708 | Unplanned | Third party interference
296 |  | 34332 | NSBT57 - WARKWORTH P280 - SANDSPIT H04 (57) | Northern | SNEL K11 | 2024-04-21 | 45403.1062 | 2024-04-21 | 45403.6875 | 0.00052715 | 0.00012621 | 79 | 330 | Unplanned | Third party interference
297 |  | 34333 | ATKI K12 - K12 GOLF RD | Northern | ATKI K12 | 2024-04-21 | 45403.1389 | 2024-04-21 | 45403.1979 | 0.013986 | 0.00016454 | 103 | 8755 | Unplanned | Vegetation
298 |  | 34335 | WOOD K05 - K05 FAIRDENE AVE | Northern | WOOD K05 | 2024-04-21 | 45403.2903 | 2024-04-21 | 45403.3229 | 0.035889 | 0.00076358 | 478 | 22466 | Unplanned | Wildlife
299 |  | 34337 | WSWA K08 - K08 COMMODORE DRIVE | Auckland | WSWA K08 | 2024-04-21 | 45403.3347 | 2024-04-21 | 45403.6632 | 0.046259 | 9.9042e-05 | 62 | 28958 | Planned | Planned
300 |  | 34339 | TPAP K16 - K16 MAYS RD | Auckland | TPAP K16 | 2024-04-21 | 45403.375 | 2024-04-21 | 45403.4326 | 0.063518 | 0.0016773 | 1050 | 39762 | Unplanned | Vegetation
301 |  | 34340 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-04-21 | 45403.6403 | 2024-04-21 | 45403.7319 | 0.00042173 | 3.195e-06 | 2 | 264 | Unplanned | Vegetation
302 |  | 34341 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K07 | 2024-04-21 | 45403.9792 | 2024-04-22 | 45404.0757 | 0.027534 | 0.00019808 | 124 | 17236 | Planned | Planned
303 |  | 34343 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-22 | 45404.3333 | 2024-04-22 | 45404.6708 | 0.027949 | 5.7505e-05 | 36 | 17496 | Planned | Planned
304 |  | 34344 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-04-22 | 45404.375 | 2024-04-22 | 45404.6771 | 0.047948 | 0.00011022 | 69 | 30015 | Planned | Planned
305 |  | 34345 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-04-22 | 45404.3819 | 2024-04-22 | 45404.6743 | 0.063218 | 0.00015016 | 94 | 39574 | Planned | Planned
306 |  | 34346 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-22 | 45404.4056 | 2024-04-22 | 45404.6229 | 0.0080001 | 2.5559e-05 | 16 | 5008 | Planned | Planned
307 |  | 34347 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-04-22 | 45404.3819 | 2024-04-22 | 45404.634 | 0.00057988 | 1.597e-06 | 1 | 363 | Planned | Planned
308 |  | 34348 | SUNS K11 - K11 PARKWAY DRIVE | Northern | SUNS K11 | 2024-04-22 | 45404.2611 | 2024-04-22 | 45404.7708 | 0.0023451 | 3.195e-06 | 2 | 1468 | Unplanned | Defective equipment
309 |  | 34349 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-04-22 | 45404.4201 | 2024-04-22 | 45404.684 | 0.0018211 | 4.792e-06 | 3 | 1140 | Planned | Planned
310 |  | 34350 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-04-22 | 45404.6451 | 2024-04-22 | 45404.6771 | 7.3483e-05 | 1.597e-06 | 1 | 46 | Unplanned | Defective equipment
311 |  | 34351 | SHOW K10 - K10 CULVER TERRACE | Auckland | SHOW K10 | 2024-04-22 | 45404.959 | 2024-04-23 | 45405.0521 | 0.013914 | 0.00010383 | 65 | 8710 | Planned | Planned
312 |  | 34352 | MCEN K03 - K03 ORLY AVE VIA LS | Auckland | MCEN K03 | 2024-04-23 | 45405.0479 | 2024-04-23 | 45405.0917 | 0.024508 | 0.0011214 | 630 | 15342 | Unplanned | Defective equipment
313 |  | 34353 | SHOW K02 - K02 GILLET PL | Auckland | SHOW K02 | 2024-04-23 | 45405.0854 | 2024-04-23 | 45405.1743 | 0.013904 | 0.00010863 | 68 | 8704 | Planned | Planned
314 |  | 34354 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2024-04-23 | 45405.1729 | 2024-04-23 | 45405.2972 | 0.0022876 | 1.2779e-05 | 8 | 1432 | Unplanned | Wildlife
315 |  | 34355 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-23 | 45405.3597 | 2024-04-23 | 45405.6674 | 0.025208 | 5.7514e-05 | 36 | 15780 | Planned | Planned
316 |  | 34356 | HOBV K04 - K04 ELIZABETH DR | Northern | HOBV K04 | 2024-04-23 | 45405.3542 | 2024-04-23 | 45405.7528 | 0.15588 | 0.00027157 | 170 | 97580 | Planned | Planned
317 |  | 34357 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-04-23 | 45405.3333 | 2024-04-23 | 45405.6854 | 0.035636 | 7.0287e-05 | 44 | 22308 | Planned | Planned
318 |  | 34358 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-04-23 | 45405.3819 | 2024-04-23 | 45405.5868 | 0.03393 | 0.00011501 | 72 | 21240 | Planned | Planned
319 |  | 34359 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-04-23 | 45405.4111 | 2024-04-23 | 45405.6424 | 0.0026598 | 7.987e-06 | 5 | 1665 | Planned | Planned
320 |  | 34360 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-04-23 | 45405.4583 | 2024-04-23 | 45405.6979 | 0.0099202 | 2.8752e-05 | 18 | 6210 | Planned | Planned
321 |  | 34362 | QUAY K23 - K23 SOFRANA HOUSE | Auckland | QUAY K23 | 2024-04-23 | 45405.9604 | 2024-04-24 | 45406.2153 | 0.11198 | 0.00030512 | 191 | 70097 | Planned | Planned
322 |  | 34363 | FREE K19 - K19 131 WELLINGTON ST | Auckland | FREE K64 | 2024-04-23 | 45405.9174 | 2024-04-24 | 45406.1562 | 0.02308 | 6.7093e-05 | 42 | 14448 | Planned | Planned
323 |  | 34364 | SHOW K06 - K06 FIELDSTONE COURT | Auckland | SHOW K06 | 2024-04-23 | 45405.9792 | 2024-04-24 | 45406.1229 | 0.042657 | 0.00020607 | 129 | 26703 | Planned | Planned
324 |  | 34365 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-24 | 45406.3542 | 2024-04-24 | 45406.7153 | 0.02492 | 4.7922e-05 | 30 | 15600 | Planned | Planned
325 |  | 34366 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-04-24 | 45406.3757 | 2024-04-24 | 45406.65 | 0.03155 | 7.9871e-05 | 50 | 19750 | Planned | Planned
326 |  | 34367 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-04-24 | 45406.375 | 2024-04-24 | 45406.6403 | 0.097637 | 0.00025559 | 160 | 61120 | Planned | Planned
327 |  | 34369 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-04-24 | 45406.3965 | 2024-04-24 | 45406.6319 | 0.061739 | 0.0003067 | 152 | 38648 | Planned | Planned
328 |  | 34370 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-04-24 | 45406.4167 | 2024-04-24 | 45406.5049 | 0.0020895 | 1.9167e-05 | 12 | 1308 | Planned | Planned
329 |  | 34371 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-04-24 | 45406.3674 | 2024-04-24 | 45406.4382 | 0.00016294 | 1.597e-06 | 1 | 102 | Unplanned | Cause unknown
330 |  | 34372 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-04-24 | 45406.425 | 2024-04-24 | 45406.6965 | 0.097439 | 0.0002492 | 156 | 60996 | Planned | Planned
331 |  | 34373 | SIMP K07 - K07 BABICH RD | Northern | SIMP K07 | 2024-04-24 | 45406.4618 | 2024-04-24 | 45406.6181 | 0.010783 | 4.7924e-05 | 30 | 6750 | Planned | Planned
332 |  | 34374 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2024-04-24 | 45406.3354 | 2024-04-26 | 45408.0347 | 0.019545 | 7.987e-06 | 5 | 12235 | Unplanned | Defective equipment
333 |  | 34375 | SIMP K08 - K08 SEIBEL ROAD | Northern | SIMP K08 | 2024-04-24 | 45406.5507 | 2024-04-24 | 45406.6215 | 0.0019553 | 1.9169e-05 | 12 | 1224 | Unplanned | Vegetation
334 |  | 34376 | PAKU K06 - K06 GOSSAMER DR | Auckland | PAKU K06 | 2024-04-24 | 45406.3958 | 2024-04-24 | 45406.6438 | 0.03935 | 0.00011022 | 69 | 24633 | Planned | Planned
335 |  | 34377 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-04-24 | 45406.375 | 2024-04-24 | 45406.6215 | 0.0022684 | 6.39e-06 | 4 | 1420 | Planned | Planned
336 |  | 34378 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2024-04-24 | 45406.6597 | 2024-04-25 | 45407.1764 | 0.13018 | 0.0014521 | 471 | 81492 | Unplanned | Third party interference
337 |  | 34379 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-04-24 | 45406.7542 | 2024-04-24 | 45406.8576 | 0.00023802 | 1.597e-06 | 1 | 149 | Unplanned | Cause unknown
338 |  | 34380 | WIRI K05 - K05 MERCK, SHARPE & DOHME VIA LS | Auckland | WIRI K05 | 2024-04-24 | 45406.8819 | 2024-04-24 | 45406.8944 | 0.0021278 | 0.00011821 | 74 | 1332 | Unplanned | Other Cause | Outage caused by Tap Operation
339 |  | 34381 | TAKA K08 - K08 GRAHAM RD | Auckland | TAKA K08 | 2024-04-24 | 45406.9792 | 2024-04-25 | 45407.1125 | 0.053675 | 0.00027956 | 175 | 33600 | Planned | Planned
340 |  | 34383 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-25 | 45407.4792 | 2024-04-25 | 45407.4944 | 3.5144e-05 | 1.597e-06 | 1 | 22 | Unplanned | Third party interference
341 |  | 34384 | KING K06 - K06 CENTRAL RD | Auckland | KING K06 | 2024-04-25 | 45407.4951 | 2024-04-25 | 45407.5444 | 0.057163 | 0.00080512 | 504 | 35784 | Unplanned | Defective equipment
342 |  | 34385 | HCRE K04 - K04 CORONATION ROAD | Northern | HCRE K04 | 2024-04-25 | 45407.5694 | 2024-04-25 | 45407.6458 | 0.012652 | 0.00011502 | 72 | 7920 | Unplanned | Defective equipment
343 |  | 34386 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-04-25 | 45407.7431 | 2024-04-25 | 45407.7514 | 0.0002492 | 2.0767e-05 | 13 | 156 | Unplanned | Vegetation
344 |  | 34388 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-26 | 45408.3771 | 2024-04-26 | 45408.6882 | 0.034352 | 7.6676e-05 | 48 | 21504 | Planned | Planned
345 |  | 34389 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-04-26 | 45408.3785 | 2024-04-26 | 45408.7271 | 0.076183 | 0.00015176 | 95 | 47690 | Planned | Planned
346 |  | 34390 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-04-26 | 45408.3854 | 2024-04-26 | 45408.6389 | 0.026821 | 7.3481e-05 | 46 | 16790 | Planned | Planned
347 |  | 34391 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-04-26 | 45408.3819 | 2024-04-26 | 45408.6451 | 0.016952 | 4.4728e-05 | 28 | 10612 | Planned | Planned
348 |  | 34392 | LIVE K11 - K11 SAPPHIRE APARTMENTS | Auckland | LIVE K11 | 2024-04-26 | 45408.3944 | 2024-04-26 | 45408.4812 | 0.071518 | 0.00059745 | 374 | 44770 | Unplanned | Third party interference
349 |  | 34393 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-04-26 | 45408.3854 | 2024-04-26 | 45408.675 | 0.0013323 | 3.195e-06 | 2 | 834 | Planned | Planned
350 |  | 34394 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-04-26 | 45408.4167 | 2024-04-26 | 45408.684 | 0.024601 | 6.3896e-05 | 40 | 15400 | Planned | Planned
351 |  | 34395 | TPAP K16 - K16 MAYS RD | Auckland | TPAP K16 | 2024-04-26 | 45408.459 | 2024-04-26 | 45408.6472 | 0.067368 | 0.0016789 | 1051 | 42172 | Unplanned | Defective equipment
352 |  | 34396 | GREE K11 - K11 CRYERS ROAD | Auckland | GREE K11 | 2024-04-26 | 45408.8875 | 2024-04-27 | 45409.0028 | 0.019911 | 0.000623 | 192 | 12464 | Unplanned | Defective equipment
353 |  | 34397 | SAND K13 - K13 2 MAYN AVE | Auckland | SAND K13 | 2024-04-27 | 45409 | 2024-04-27 | 45409.2299 | 0.031197 | 9.4249e-05 | 59 | 19529 | Planned | Planned
354 |  | 34399 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-04-26 | 45408.8993 | 2024-04-27 | 45409.4618 | 0 | 0 | 0 | 0 | Unplanned | Defective equipment
355 |  | 34400 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-04-27 | 45409.3368 | 2024-04-27 | 45409.7674 | 0.010895 | 1.7572e-05 | 11 | 6820 | Planned | Planned
356 |  | 34401 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-04-27 | 45409.375 | 2024-04-27 | 45409.7174 | 0.054341 | 0.00011022 | 69 | 34017 | Planned | Planned
357 |  | 34402 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-04-27 | 45409.3771 | 2024-04-27 | 45409.7167 | 0.015623 | 3.1948e-05 | 20 | 9780 | Planned | Planned
358 |  | 34403 | SAND K18 - K18 SANDRINGHAM RD EXTN - SOUTH | Auckland | SAND K18 | 2024-04-27 | 45409.3958 | 2024-04-27 | 45409.7514 | 0.18975 | 0.00037061 | 232 | 118784 | Planned | Planned
359 |  | 34404 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2024-04-27 | 45409.4639 | 2024-04-27 | 45409.5069 | 0.080669 | 0.002516 | 1575 | 50498 | Unplanned | Cause unknown
360 |  | 34407 | WAIR K12 - K12 ARCHERS ROAD | Northern | WAIR K12 | 2024-04-28 | 45410.216 | 2024-04-28 | 45410.4597 | 0.0033642 | 9.585e-06 | 6 | 2106 | Planned | Planned
361 |  | 34408 | WAIR K12 - K12 ARCHERS ROAD | Northern | WAIR K12 | 2024-04-28 | 45410.3396 | 2024-04-28 | 45410.7965 | 0.55605 | 0.00084506 | 529 | 348082 | Planned | Planned
362 |  | 34409 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-04-28 | 45410.4049 | 2024-04-28 | 45410.4528 | 0.00011022 | 1.597e-06 | 1 | 69 | Unplanned | Wildlife
363 |  | 34410 | WAIM K05 - K05 MURIWAI | Northern | WAIM K08 | 2024-04-28 | 45410.909 | 2024-04-29 | 45411.1181 | 0.050007 | 0.00016613 | 104 | 31304 | Unplanned | Defective equipment
364 |  | 34411 | WIRI K15 - K15 KEITH HAY DR | Auckland | WIRI K15 | 2024-04-28 | 45410.9167 | 2024-04-29 | 45411.0125 | 0.018297 | 0.00013259 | 83 | 11454 | Planned | Planned
365 |  | 34412 | WAIR K12 - K12 ARCHERS ROAD | Northern | WAIR K12 | 2024-04-29 | 45411.2083 | 2024-04-29 | 45411.2264 | 0.0002492 | 9.585e-06 | 6 | 156 | Planned | Planned
366 |  | 34413 | RIVE K04 - K04 BARRETT RD | Northern | RIVE K04 | 2024-04-29 | 45411.3125 | 2024-04-29 | 45411.7208 | 0.032272 | 0.00056552 | 179 | 20202 | Planned | Planned
367 |  | 34414 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-04-29 | 45411.3868 | 2024-04-29 | 45411.6333 | 0.0005671 | 1.597e-06 | 1 | 355 | Planned | Planned
368 |  | 34416 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-04-29 | 45411.4167 | 2024-04-29 | 45411.6778 | 0.036039 | 9.5844e-05 | 60 | 22560 | Planned | Planned
369 |  | 34417 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-04-29 | 45411.4201 | 2024-04-29 | 45411.7278 | 0.0049537 | 1.118e-05 | 7 | 3101 | Planned | Planned
370 |  | 34418 | BOMA - Big Omaha | Northern | BOMA K01 | 2024-04-29 | 45411.4354 | 2024-04-29 | 45411.5062 | 0.027821 | 0.0039746 | 2488 | 17416 | Unplanned | Wildlife
371 |  | 34418 | BOMA - Big Omaha | Northern | BOMA K04 | 2024-04-29 | 45411.4354 | 2024-04-29 | 45411.5062 | 0.0042412 | 0.0014137 | 885 | 2655 | Unplanned | Wildlife
372 |  | 34418 | BOMA - Big Omaha | Northern | BOMA K06 | 2024-04-29 | 45411.4354 | 2024-04-29 | 45411.5062 | 0.00016294 | 1.596e-06 | 1 | 102 | Unplanned | Wildlife
373 |  | 34419 | FREE K08 - K08 BEAUMONT ST | Auckland | FREE K52 | 2024-04-29 | 45411.5833 | 2024-04-29 | 45411.6007 | 0.0053515 | 0.00021406 | 134 | 3350 | Planned | Planned
374 |  | 34420 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-04-29 | 45411.7611 | 2024-04-29 | 45411.8201 | 0.0010863 | 1.2779e-05 | 8 | 680 | Unplanned | Cause unknown
375 |  | 34421 | KEEL K06 - K06 HICKORY AVE | Northern | KEEL K06 | 2024-04-29 | 45411.8333 | 2024-04-30 | 45412.2028 | 0.028845 | 5.4313e-05 | 34 | 18057 | Planned | Planned
376 |  | 34422 | BALM K05 - K05 BRIXTON ROAD | Auckland | BALM K05 | 2024-04-29 | 45411.9799 | 2024-04-30 | 45412.191 | 0.080614 | 0.00026518 | 166 | 50464 | Planned | Planned
377 |  | 34423 | PAPA K10 - K10 17 PORCHESTER RD | Auckland | PAPA K10 | 2024-04-29 | 45411.9174 | 2024-04-29 | 45411.9688 | 0.0020096 | 2.7157e-05 | 17 | 1258 | Unplanned | Defective equipment
378 |  | 34424 | HANS K05 - K05 KRAFT FOODS | Auckland | HANS K05 | 2024-04-30 | 45412.2083 | 2024-04-30 | 45412.2778 | 0.03142 | 0.00037061 | 232 | 19669 | Planned | Planned
379 |  | 34425 | VICT K14 - K14 KITCHENER TOWERS & CAP BANK | Auckland | VICT K14 | 2024-04-30 | 45412.2757 | 2024-04-30 | 45412.4222 | 0.25365 | 0.0028802 | 889 | 158783 | Unplanned | Cause unknown
380 |  | 34426 | ECOA K07 - K07 OAKTREE AVENUE | Northern | ECOA K07 | 2024-04-30 | 45412.3618 | 2024-04-30 | 45412.3965 | 0.0089458 | 0.00017892 | 112 | 5600 | Unplanned | Defective equipment
381 |  | 34427 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-04-30 | 45412.375 | 2024-04-30 | 45412.7188 | 0.003163 | 6.39e-06 | 4 | 1980 | Planned | Planned
382 |  | 34428 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-04-30 | 45412.3542 | 2024-04-30 | 45412.7049 | 0.0040336 | 7.987e-06 | 5 | 2525 | Planned | Planned
383 |  | 34429 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-04-30 | 45412.375 | 2024-04-30 | 45412.6292 | 0.0011693 | 3.195e-06 | 2 | 732 | Planned | Planned
384 |  | 34430 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-04-30 | 45412.3854 | 2024-04-30 | 45412.5285 | 0.00032908 | 1.597e-06 | 1 | 206 | Planned | Planned
385 |  | 34431 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-04-30 | 45412.3333 | 2024-04-30 | 45412.6687 | 0.097218 | 0.00020127 | 126 | 60858 | Planned | Planned
386 |  | 34432 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-04-30 | 45412.3826 | 2024-04-30 | 45412.7361 | 0.10489 | 0.00020607 | 129 | 65661 | Planned | Planned
387 |  | 34433 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-04-30 | 45412.375 | 2024-04-30 | 45412.6389 | 0.032641 | 0.0028898 | 916 | 20433 | Planned | Planned
388 |  | 34434 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-04-30 | 45412.4236 | 2024-04-30 | 45412.566 | 0.03897 | 0.0001901 | 119 | 24395 | Planned | Planned
389 |  | 34435 | WAIR K04 - K04 HILLSIDE ROAD | Northern | WAIR K04 | 2024-04-30 | 45412.45 | 2024-04-30 | 45412.6826 | 0.022109 | 0.00030672 | 141 | 13840 | Unplanned | Cause unknown
390 |  | 34436 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-04-30 | 45412.3743 | 2024-04-30 | 45412.5069 | 0.0018307 | 9.585e-06 | 6 | 1146 | Unplanned | Cause unknown
391 |  | 34438 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-04-30 | 45412.8215 | 2024-04-30 | 45412.9271 | 0.0012141 | 7.987e-06 | 5 | 760 | Unplanned | Cause unknown
392 |  | 34439 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-05-01 | 45413.3826 | 2024-05-01 | 45413.7014 | 0.27423 | 0.00059745 | 374 | 171666 | Planned | Planned
393 |  | 34440 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-05-01 | 45413.375 | 2024-05-01 | 45413.6687 | 0.00067572 | 1.597e-06 | 1 | 423 | Planned | Planned
394 |  | 34441 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-01 | 45413.375 | 2024-05-01 | 45413.3819 | 1.5975e-05 | 1.597e-06 | 1 | 10 | Planned | Planned
395 |  | 34442 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-05-01 | 45413.3993 | 2024-05-01 | 45413.7118 | 0.019409 | 4.3129e-05 | 27 | 12150 | Planned | Planned
396 |  | 34443 | GREE K02 - K02 GUYS RD | Auckland | GREE K02 | 2024-05-01 | 45413.4187 | 2024-05-01 | 45413.5632 | 0.021598 | 0.00010383 | 65 | 13520 | Planned | Planned
397 |  | 34444 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-05-01 | 45413.4194 | 2024-05-01 | 45413.4222 | 0.0073307 | 0.0024122 | 1510 | 4589 | Unplanned | Third party interference
398 |  | 34445 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-05-01 | 45413.3986 | 2024-05-01 | 45413.734 | 0.022376 | 4.6326e-05 | 29 | 14007 | Planned | Planned
399 |  | 34446 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-01 | 45413.4375 | 2024-05-01 | 45413.4444 | 0.00014377 | 1.4377e-05 | 9 | 90 | Planned | Planned
400 |  | 34447 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-01 | 45413.4792 | 2024-05-01 | 45413.4861 | 3.1949e-05 | 3.195e-06 | 2 | 20 | Planned | Planned
401 |  | 34448 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-01 | 45413.4931 | 2024-05-01 | 45413.5 | 4.7924e-05 | 4.792e-06 | 3 | 30 | Planned | Planned
402 |  | 34449 | HCRE K02 - K02 FOWLER STREET | Northern | HCRE K02 | 2024-05-02 | 45414.0208 | 2024-05-02 | 45414.3104 | 0.27651 | 0.0023595 | 1477 | 173094 | Unplanned | Defective equipment
403 |  | 34449 | HCRE K02 - K02 FOWLER STREET | Northern | NCOT K01 | 2024-05-02 | 45414.0208 | 2024-05-02 | 45414.3104 | 0.023794 | 7.1886e-05 | 45 | 14895 | Unplanned | Defective equipment
404 |  | 34450 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-05-02 | 45414.1535 | 2024-05-02 | 45414.375 | 0.0045863 | 1.4376e-05 | 9 | 2871 | Unplanned | Cause unknown
405 |  | 34451 | HANS K05 - K05 KRAFT FOODS | Auckland | HANS K05 | 2024-05-02 | 45414.2083 | 2024-05-02 | 45414.2792 | 0.025419 | 0.0002492 | 156 | 15912 | Planned | Planned
406 |  | 34452 | BMON K04 - K04 GRAMMAR SCHOOL + LS | Northern | BMON K04 | 2024-05-02 | 45414.2083 | 2024-05-02 | 45414.7188 | 0.23065 | 0.00089138 | 461 | 144385 | Planned | Planned
407 |  | 34453 | RBEA K05 - K05 JELAS RD | Northern | RBEA K05 | 2024-05-02 | 45414.3139 | 2024-05-02 | 45414.6819 | 0.26647 | 0.00076997 | 395 | 166807 | Planned | Planned
408 |  | 34454 | WAIA K05 - K05 CARLISE ROAD | Northern | WAIA K05 | 2024-05-02 | 45414.3333 | 2024-05-02 | 45414.6903 | 0.009032 | 1.7572e-05 | 11 | 5654 | Planned | Planned
409 |  | 34455 | RIVE K11 - K11 CARTERS MILL | Northern | RIVE K11 | 2024-05-02 | 45414.1424 | 2024-05-02 | 45414.3646 | 0.00051119 | 1.597e-06 | 1 | 320 | Unplanned | Vegetation
410 |  | 34456 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-02 | 45414.3542 | 2024-05-02 | 45414.6965 | 0.10081 | 0.00020448 | 128 | 63104 | Planned | Planned
411 |  | 34457 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-05-02 | 45414.375 | 2024-05-02 | 45414.6951 | 0.005155 | 1.1182e-05 | 7 | 3227 | Planned | Planned
412 |  | 34458 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-02 | 45414.375 | 2024-05-02 | 45414.6042 | 0.23564 | 0.00071406 | 447 | 147510 | Planned | Planned
413 |  | 34459 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-02 | 45414.3333 | 2024-05-02 | 45414.6604 | 0.027087 | 5.7505e-05 | 36 | 16956 | Planned | Planned
414 |  | 34460 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-05-02 | 45414.375 | 2024-05-02 | 45414.7431 | 0.0127 | 2.396e-05 | 15 | 7950 | Planned | Planned
415 |  | 34461 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-05-02 | 45414.3167 | 2024-05-02 | 45414.4097 | 0.00064218 | 4.792e-06 | 3 | 402 | Unplanned | Wildlife
416 |  | 34462 | ONEH K01 - K01 - PAYNES LANE | Auckland | ONEH K01 | 2024-05-02 | 45414.4014 | 2024-05-02 | 45414.6146 | 0.025011 | 8.147e-05 | 51 | 15657 | Planned | Planned
417 |  | 34463 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-05-02 | 45414.4576 | 2024-05-02 | 45414.5465 | 0.012882 | 0.00010064 | 63 | 8064 | Unplanned | Vegetation
418 |  | 34464 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-02 | 45414.341 | 2024-05-02 | 45414.5035 | 0.0014952 | 6.389e-06 | 4 | 936 | Unplanned | Cause unknown
419 |  | 34465 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2024-05-02 | 45414.5708 | 2024-05-02 | 45414.75 | 0.13353 | 0.0014681 | 919 | 83586 | Unplanned | Defective equipment
420 |  | 34467 | WELL K02 - K02 TOMARATA | Northern | BOMA K04 | 2024-05-02 | 45414.6604 | 2024-05-02 | 45414.9917 | 0.049441 | 0.00098882 | 619 | 30950 | Unplanned | Defective equipment
421 |  | 34467 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-05-02 | 45414.6604 | 2024-05-02 | 45414.9917 | 0.078098 | 0.00091212 | 571 | 48889 | Unplanned | Defective equipment
422 |  | 34467 | WELL K02 - K02 TOMARATA | Northern | WELL K07 | 2024-05-02 | 45414.6604 | 2024-05-02 | 45414.9917 | 0.0041933 | 2.396e-05 | 15 | 2625 | Unplanned | Defective equipment
423 |  | 34468 | KEEL K06 - K06 HICKORY AVE | Northern | KEEL K06 | 2024-05-02 | 45414.8333 | 2024-05-03 | 45415.2326 | 0.031131 | 5.4313e-05 | 34 | 19488 | Planned | Planned
424 |  | 34469 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-05-03 | 45415.1736 | 2024-05-03 | 45415.2444 | 0.025697 | 0.000254 | 159 | 16086 | Planned | Planned
425 |  | 34470 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-05-03 | 45415.3368 | 2024-05-03 | 45415.6597 | 0.035774 | 8.626e-05 | 54 | 22394 | Planned | Planned
426 |  | 34471 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-05-03 | 45415.375 | 2024-05-03 | 45415.6042 | 0.057988 | 0.00017572 | 110 | 36300 | Planned | Planned
427 |  | 34472 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-05-03 | 45415.375 | 2024-05-03 | 45415.6882 | 0.014409 | 3.1948e-05 | 20 | 9020 | Planned | Planned
428 |  | 34473 | RIVE K11 - K11 CARTERS MILL | Northern | RIVE K11 | 2024-05-03 | 45415.375 | 2024-05-03 | 45415.6972 | 0.00074122 | 1.597e-06 | 1 | 464 | Planned | Planned
429 |  | 34474 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-05-03 | 45415.3778 | 2024-05-03 | 45415.6354 | 0.00059266 | 1.597e-06 | 1 | 371 | Planned | Planned
430 |  | 34475 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-03 | 45415.3764 | 2024-05-03 | 45415.6271 | 0.00173 | 4.792e-06 | 3 | 1083 | Planned | Planned
431 |  | 34477 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-05-03 | 45415.3868 | 2024-05-03 | 45415.7583 | 0.0042732 | 7.987e-06 | 5 | 2675 | Planned | Planned
432 |  | 34478 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-05-03 | 45415.4375 | 2024-05-03 | 45415.4618 | 5.5911e-05 | 1.597e-06 | 1 | 35 | Unplanned | Defective equipment
433 |  | 34480 | RBEA K03 - K03 BAY ST | Northern | RBEA K03 | 2024-05-03 | 45415.834 | 2024-05-03 | 45415.8389 | 0.00015655 | 2.2364e-05 | 14 | 98 | Unplanned | Other Cause | Outage caused by Tap Operation
434 |  | 34481 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-03 | 45415.8889 | 2024-05-03 | 45415.9944 | 0.00048563 | 3.195e-06 | 2 | 304 | Unplanned | Defective equipment
435 |  | 34482 | PARN K05 - K05 GIBRALTAR CRES | Auckland | PARN K05 | 2024-05-03 | 45415.9167 | 2024-05-04 | 45416.0069 | 0.020352 | 0.00015655 | 98 | 12740 | Planned | Planned
436 |  | 34483 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-05-04 | 45416.316 | 2024-05-04 | 45416.5528 | 0.067333 | 0.00063259 | 396 | 42150 | Unplanned | Vegetation
437 |  | 34484 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-04 | 45416.3556 | 2024-05-04 | 45416.6146 | 0.025622 | 6.8689e-05 | 43 | 16039 | Planned | Planned
438 |  | 34485 | MCEN K01 - K01 MANGERE BRIDGE | Auckland | MCEN K01 | 2024-05-04 | 45416.3792 | 2024-05-04 | 45416.6576 | 0.080073 | 0.00019968 | 125 | 50125 | Planned | Planned
439 |  | 34486 | TRIA K10 - K10 WEST | Northern | TRIA K10 | 2024-05-04 | 45416.3639 | 2024-05-04 | 45416.7396 | 0.06783 | 0.00019329 | 81 | 42461 | Planned | Planned
440 |  | 34487 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-05-04 | 45416.375 | 2024-05-04 | 45416.6736 | 0.096854 | 0.00022524 | 141 | 60630 | Planned | Planned
441 |  | 34488 | ORAK K11 - K11 KOHIMARAMA RD | Auckland | ORAK K11 | 2024-05-04 | 45416.4028 | 2024-05-04 | 45416.4396 | 0.015324 | 0.00028914 | 181 | 9593 | Planned | Planned
442 |  | 34489 | TAKA K13 - K13 COSGROVE RD | Auckland | TAKA K13 | 2024-05-04 | 45416.325 | 2024-05-04 | 45416.4306 | 0.0012141 | 7.987e-06 | 5 | 760 | Unplanned | Vegetation
443 |  | 34490 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2024-05-04 | 45416.4799 | 2024-05-04 | 45416.5083 | 0.10419 | 0.0039409 | 2467 | 65220 | Unplanned | Third party interference
444 |  | 34492 | HANS K29 - K29 KAKA COMMERCIAL | Auckland | HANS K29 | 2024-05-04 | 45416.7583 | 2024-05-06 | 45418.4125 | 0.0038051 | 1.597e-06 | 1 | 2382 | Unplanned | Defective equipment
445 |  | 34493 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-05-04 | 45416.9965 | 2024-05-05 | 45417.1931 | 0.015823 | 5.5912e-05 | 35 | 9905 | Unplanned | Third party interference
446 |  | 34494 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-05 | 45417.3854 | 2024-05-05 | 45417.4771 | 0.003163 | 2.3962e-05 | 15 | 1980 | Unplanned | Cause unknown
447 |  | 34495 | NEWM K01 - K01 EDUCATIONAL DEPT VIA LS | Auckland | NEWM K01 | 2024-05-05 | 45417.6618 | 2024-05-05 | 45417.8611 | 0.24193 | 0.0021326 | 1335 | 151446 | Unplanned | Third party interference
448 |  | 34496 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-05-06 | 45418.0104 | 2024-05-06 | 45418.1632 | 0.065815 | 0.0012077 | 756 | 41200 | Unplanned | Cause unknown
449 |  | 34497 | NSBT92 - TP ALBANY 2142- COATESVILLE H02 (92) | Northern | COAT K12 | 2024-05-06 | 45418.3333 | 2024-05-06 | 45418.6937 | 0.25901 | 0.00051277 | 321 | 162140 | Planned | Planned
450 |  | 34498 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2024-05-06 | 45418.375 | 2024-05-06 | 45418.7889 | 0.36941 | 0.00061981 | 388 | 231248 | Planned | Planned
451 |  | 34499 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-05-06 | 45418.3785 | 2024-05-06 | 45418.6403 | 0.013984 | 4.3132e-05 | 27 | 8754 | Planned | Planned
452 |  | 34500 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-05-06 | 45418.375 | 2024-05-06 | 45418.7257 | 0.0048403 | 9.585e-06 | 6 | 3030 | Planned | Planned
453 |  | 34501 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-05-06 | 45418.4479 | 2024-05-06 | 45418.6111 | 0.0003754 | 1.597e-06 | 1 | 235 | Planned | Planned
454 |  | 34502 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2024-05-06 | 45418.4604 | 2024-05-06 | 45418.5333 | 0.23807 | 0.0038962 | 2439 | 149028 | Unplanned | Cause unknown
455 |  | 34503 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-05-06 | 45418.5326 | 2024-05-06 | 45418.7493 | 0.041457 | 0.0013643 | 854 | 25952 | Unplanned | Wildlife
456 |  | 34504 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-05-06 | 45418.4167 | 2024-05-06 | 45418.6979 | 0.12939 | 0.00031948 | 200 | 81000 | Planned | Planned
457 |  | 34505 | MKAU K22 - K22 GREAT SOUTH ROAD | Auckland | MKAU K22 | 2024-05-06 | 45418.9792 | 2024-05-07 | 45419.191 | 0.3318 | 0.0010879 | 681 | 207705 | Planned | Planned
458 |  | 34506 | WAIA K01 - K01 MIZPAH ROAD | Northern | WAIA K01 | 2024-05-07 | 45419.3951 | 2024-05-07 | 45419.7431 | 0.11994 | 0.00069649 | 436 | 75084 | Unplanned | Third party interference
459 |  | 34507 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-07 | 45419.2701 | 2024-05-07 | 45419.3313 | 0.0015463 | 1.7572e-05 | 11 | 968 | Unplanned | Wildlife
460 |  | 34508 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-05-07 | 45419.375 | 2024-05-07 | 45419.6569 | 0.067451 | 0.00016613 | 104 | 42224 | Planned | Planned
461 |  | 34509 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-05-07 | 45419.3854 | 2024-05-07 | 45419.5938 | 0.00095848 | 3.195e-06 | 2 | 600 | Planned | Planned
462 |  | 34510 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-05-07 | 45419.4062 | 2024-05-07 | 45419.5556 | 0.00034345 | 1.597e-06 | 1 | 215 | Planned | Planned
463 |  | 34511 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-07 | 45419.4153 | 2024-05-07 | 45419.5625 | 0.00033866 | 1.597e-06 | 1 | 212 | Planned | Planned
464 |  | 34512 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2024-05-07 | 45419.4292 | 2024-05-07 | 45419.4604 | 0.028011 | 0.00080991 | 507 | 17535 | Unplanned | Cause unknown
465 |  | 34513 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-07 | 45419.3785 | 2024-05-07 | 45419.4944 | 0.00026678 | 1.597e-06 | 1 | 167 | Planned | Planned
466 |  | 34514 | ROSE K16 - K16 432 ROSEBANK RD | Auckland | ROSE K16 | 2024-05-07 | 45419.8819 | 2024-05-07 | 45419.9632 | 0.001869 | 1.5974e-05 | 10 | 1170 | Unplanned | Third party interference
467 |  | 34515 | PARN K05 - K05 GIBRALTAR CRES | Auckland | PARN K05 | 2024-05-07 | 45419.959 | 2024-05-08 | 45420.1243 | 0.0022812 | 9.585e-06 | 6 | 1428 | Planned | Planned
468 |  | 34516 | MNAB K16 - K16 GLASS RECYCLERS | Auckland | MNAB K16 | 2024-05-07 | 45419.9653 | 2024-05-08 | 45420.0312 | 0.0045528 | 4.7923e-05 | 30 | 2850 | Planned | Planned
469 |  | 34517 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-08 | 45420.3361 | 2024-05-08 | 45420.5958 | 0.027483 | 7.3478e-05 | 46 | 17204 | Planned | Planned
470 |  | 34518 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2024-05-08 | 45420.3042 | 2024-05-08 | 45420.7285 | 0.18086 | 0.00032748 | 205 | 113219 | Planned | Planned
471 |  | 34519 | MWES K02 - K02 ORUARANGI RD | Auckland | MWES K02 | 2024-05-08 | 45420.3958 | 2024-05-08 | 45420.4597 | 0.0008818 | 9.584e-06 | 6 | 552 | Planned | Planned
472 |  | 34520 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-05-08 | 45420.4167 | 2024-05-08 | 45420.5757 | 0.051946 | 0.00022684 | 142 | 32518 | Planned | Planned
473 |  | 34521 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-08 | 45420.4792 | 2024-05-08 | 45420.4896 | 0.00014377 | 9.585e-06 | 6 | 90 | Planned | Planned
474 |  | 34522 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-08 | 45420.5625 | 2024-05-08 | 45420.575 | 0.00014377 | 7.987e-06 | 5 | 90 | Planned | Planned
475 |  | 34523 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-08 | 45420.6458 | 2024-05-08 | 45420.6528 | 4.7924e-05 | 4.792e-06 | 3 | 30 | Planned | Planned
476 |  | 34525 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-08 | 45420.5944 | 2024-05-08 | 45420.6632 | 0.0003163 | 3.195e-06 | 2 | 198 | Unplanned | Third party interference
477 |  | 34526 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-05-08 | 45420.4465 | 2024-05-08 | 45420.6667 | 0.0015192 | 4.792e-06 | 3 | 951 | Planned | Planned
478 |  | 34527 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-05-08 | 45420.916 | 2024-05-08 | 45420.9201 | 5.7509e-05 | 9.585e-06 | 6 | 36 | Unplanned | Other Cause | Outage caused by Tap Operation
479 |  | 34528 | MANL K01 - K01 ARMY BAY | Northern | MANL K01 | 2024-05-09 | 45421.375 | 2024-05-09 | 45421.5222 | 0.019981 | 9.425e-05 | 59 | 12508 | Planned | Planned
480 |  | 34529 | NLYN K01 - K01 ARAWA ST | Northern | NLYN K01 | 2024-05-09 | 45421.3965 | 2024-05-09 | 45421.5306 | 0.076461 | 0.00039617 | 248 | 47864 | Planned | Planned
481 |  | 34530 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-09 | 45421.3958 | 2024-05-09 | 45421.7049 | 0.023459 | 5.2714e-05 | 33 | 14685 | Planned | Planned
482 |  | 34531 | WSWA K06 - K06 ROSKILL RIPPLE | Auckland | WSWA K06 | 2024-05-09 | 45421.3778 | 2024-05-09 | 45421.7278 | 0.035583 | 0.00014377 | 45 | 22275 | Planned | Planned
483 |  | 34532 | PONS K12 - K12 RICHMOND ROAD | Auckland | PONS K12 | 2024-05-09 | 45421.441 | 2024-05-09 | 45421.7451 | 0.19311 | 0.0004409 | 276 | 120888 | Planned | Planned
484 |  | 34533 | GREE K02 - K02 GUYS RD | Auckland | GREE K02 | 2024-05-09 | 45421.459 | 2024-05-09 | 45421.4785 | 0.0029074 | 0.00010383 | 65 | 1820 | Planned | Planned
485 |  | 34534 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-05-09 | 45421.4458 | 2024-05-09 | 45421.4493 | 4.7924e-05 | 9.585e-06 | 6 | 30 | Unplanned | Other Cause | Outage caused by Tap Operation
486 |  | 34535 | HCRE K11 - K11 KILLARNEY STREET | Northern | HCRE K11 | 2024-05-09 | 45421.5493 | 2024-05-09 | 45421.6389 | 0.0063882 | 4.9521e-05 | 31 | 3999 | Unplanned | Cause unknown
487 |  | 34536 | SPUR K02 - K02 REDVALE | Northern | MKIN K11 | 2024-05-09 | 45421.666 | 2024-05-09 | 45421.7111 | 0.0058787 | 0.0011757 | 736 | 3680 | Unplanned | Cause unknown
488 |  | 34536 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-05-09 | 45421.666 | 2024-05-09 | 45421.7111 | 0.024438 | 0.0019233 | 1204 | 15298 | Unplanned | Cause unknown
489 |  | 34537 | ECOA K07 - K07 OAKTREE AVENUE | Northern | ECOA K07 | 2024-05-09 | 45421.9181 | 2024-05-10 | 45422.2125 | 0.11447 | 0.00026997 | 169 | 71656 | Planned | Planned
490 |  | 34539 | ONEH K02 - K02 - GALWAY ST | Auckland | ONEH K02 | 2024-05-09 | 45421.9167 | 2024-05-10 | 45422.1597 | 0.0027956 | 7.987e-06 | 5 | 1750 | Planned | Planned
491 |  | 34540 | SHEL K06 - K06 RIDDELL RD EAST | Auckland | SHEL K06 | 2024-05-09 | 45421.9382 | 2024-05-10 | 45422.2201 | 0.029834 | 7.3483e-05 | 46 | 18676 | Planned | Planned
492 |  | 34542 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-05-10 | 45422.3757 | 2024-05-10 | 45422.6806 | 0.029454 | 6.7089e-05 | 42 | 18438 | Planned | Planned
493 |  | 34543 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-05-10 | 45422.375 | 2024-05-10 | 45422.55 | 0.00080512 | 3.195e-06 | 2 | 504 | Planned | Planned
494 |  | 34544 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-10 | 45422.375 | 2024-05-10 | 45422.7104 | 0.0015431 | 3.195e-06 | 2 | 966 | Planned | Planned
495 |  | 34545 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-10 | 45422.375 | 2024-05-10 | 45422.6757 | 0.012451 | 2.8753e-05 | 18 | 7794 | Planned | Planned
496 |  | 34547 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-05-10 | 45422.375 | 2024-05-10 | 45422.7632 | 0.0026789 | 4.792e-06 | 3 | 1677 | Planned | Planned
497 |  | 34548 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-05-10 | 45422.3958 | 2024-05-10 | 45422.6368 | 0.0011086 | 3.195e-06 | 2 | 694 | Planned | Planned
498 |  | 34549 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-05-10 | 45422.3958 | 2024-05-10 | 45422.6889 | 0.005393 | 1.278e-05 | 8 | 3376 | Planned | Planned
499 |  | 34550 | NSBT92 - TP ALBANY 2142- COATESVILLE H02 (92) | Northern | COAT K12 | 2024-05-10 | 45422.5 | 2024-05-10 | 45422.616 | 0.080173 | 0.0005144 | 322 | 50188 | Planned | Planned
500 |  | 34551 | SUNS K11 - K11 PARKWAY DRIVE | Northern | SUNS K11 | 2024-05-10 | 45422.5194 | 2024-05-10 | 45422.9896 | 0.0018658 | 3.1949e-05 | 20 | 1168 | Unplanned | Defective equipment
501 |  | 34552 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2024-05-10 | 45422.6847 | 2024-05-10 | 45422.7236 | 0.0055464 | 9.9042e-05 | 62 | 3472 | Unplanned | Defective equipment
502 |  | 34553 | GREE K06 - K06 88 HARRIS RD | Auckland | GREE K06 | 2024-05-10 | 45422.9167 | 2024-05-11 | 45423.2604 | 0.0015815 | 3.195e-06 | 2 | 990 | Planned | Planned
503 |  | 34554 | SAND K18 - K18 SANDRINGHAM RD EXTN - SOUTH | Auckland | SAND K18 | 2024-05-10 | 45422.9583 | 2024-05-11 | 45423.2715 | 0.11023 | 0.00024441 | 153 | 69003 | Planned | Planned
504 |  | 34555 | NEWT K18 - K18 SYMONDS ST 226 | Auckland | NEWT K18 | 2024-05-11 | 45423.0174 | 2024-05-11 | 45423.266 | 0.00057189 | 1.597e-06 | 1 | 358 | Planned | Planned
505 |  | 34556 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-11 | 45423.2306 | 2024-05-11 | 45423.7535 | 0.048171 | 0.00020288 | 95 | 30155 | Planned | Planned
506 |  | 34557 | HPOI K06 - K06 WISELEY RD | Northern | HPOI K06 | 2024-05-11 | 45423.3021 | 2024-05-11 | 45423.8458 | 0.11737 | 0.0018259 | 1063 | 73474 | Planned | Planned
507 |  | 34558 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-11 | 45423.3576 | 2024-05-11 | 45423.7306 | 0.076347 | 0.00014217 | 89 | 47793 | Planned | Planned
508 |  | 34559 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-05-11 | 45423.3542 | 2024-05-11 | 45423.6875 | 0.035272 | 7.3482e-05 | 46 | 22080 | Planned | Planned
509 |  | 34560 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-05-11 | 45423.375 | 2024-05-11 | 45423.6528 | 0.013419 | 3.3546e-05 | 21 | 8400 | Planned | Planned
510 |  | 34561 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-11 | 45423.375 | 2024-05-11 | 45423.6903 | 0.045691 | 0.00010063 | 63 | 28602 | Planned | Planned
511 |  | 34562 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-11 | 45423.3611 | 2024-05-11 | 45423.6882 | 0.11286 | 0.00023962 | 150 | 70650 | Planned | Planned
512 |  | 34563 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-05-11 | 45423.2639 | 2024-05-11 | 45423.3854 | 0.00055911 | 3.195e-06 | 2 | 350 | Unplanned | Wildlife
513 |  | 34564 | FORR K02 - K02 CASTOR BAY | Northern | FORR K02 | 2024-05-11 | 45423.7 | 2024-05-11 | 45423.7361 | 0.022403 | 0.0016965 | 1062 | 14024 | Unplanned | Cause unknown
514 |  | 34565 | MILF K04 - K04 ALMA RD | Northern | MILF K04 | 2024-05-12 | 45424.3382 | 2024-05-12 | 45424.6722 | 0.0038419 | 7.987e-06 | 5 | 2405 | Planned | Planned
515 |  | 34566 | PAPA K06 - K06 13 PORCHESTER RD | Auckland | PAPA K06 | 2024-05-12 | 45424.375 | 2024-05-12 | 45424.8493 | 0.0067477 | 2.8752e-05 | 11 | 4224 | Planned | Planned
516 |  | 34567 | WAIR K06 - K06 DIANA DRIVE | Northern | WAIR K06 | 2024-05-12 | 45424.4083 | 2024-05-12 | 45424.5993 | 0.0050384 | 0.00021246 | 76 | 3154 | Unplanned | Defective equipment
517 |  | 34568 | MANU K04 - K04 CENTRE WEYMOUTH RD VIA LS | Auckland | MANU K04 | 2024-05-12 | 45424.4097 | 2024-05-12 | 45424.5722 | 0.16132 | 0.0025464 | 1594 | 100984 | Unplanned | Defective equipment
518 |  | 34570 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-05-12 | 45424.8486 | 2024-05-13 | 45425.1424 | 0.020947 | 4.9521e-05 | 31 | 13113 | Planned | Planned
519 |  | 34571 | CLEN K07 - K07 ROBERT ROSS | Auckland | CLEN K07 | 2024-05-12 | 45424.9583 | 2024-05-13 | 45425.0451 | 0.039537 | 0.0003163 | 198 | 24750 | Planned | Planned
520 |  | 34572 | AVON K05 - K05 BLOCKHOUSE BAY RD. NORTH | Auckland | AVON K05 | 2024-05-12 | 45424.9597 | 2024-05-12 | 45424.9979 | 0.023107 | 0.00042013 | 263 | 14465 | Planned | Planned
521 |  | 34573 | BAIR K09 - K09 CARTER HOLT | Auckland | BAIR K09 | 2024-05-13 | 45425.0833 | 2024-05-13 | 45425.1632 | 0.00091854 | 7.987e-06 | 5 | 575 | Planned | Planned
522 |  | 34574 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-05-13 | 45425.4187 | 2024-05-13 | 45425.7132 | 0.037253 | 8.7858e-05 | 55 | 23320 | Planned | Planned
523 |  | 34575 | HANS K08 - K08 MANGERE RD | Auckland | HANS K08 | 2024-05-13 | 45425.8389 | 2024-05-14 | 45426.1944 | 0.033256 | 6.5498e-05 | 41 | 20818 | Planned | Planned
524 |  | 34576 | CLEN K09 - K09 WEYMOUTH SOUTH | Auckland | CLEN K09 | 2024-05-13 | 45425.9583 | 2024-05-14 | 45426.0347 | 0.01353 | 0.000123 | 77 | 8470 | Planned | Planned
525 |  | 34577 | HANS K05 - K05 KRAFT FOODS | Auckland | HANS K05 | 2024-05-13 | 45425.9812 | 2024-05-14 | 45426.0437 | 0.0023003 | 2.5559e-05 | 16 | 1440 | Planned | Planned
526 |  | 34578 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-05-14 | 45426.0833 | 2024-05-14 | 45426.1597 | 0.024777 | 0.00022524 | 141 | 15510 | Planned | Planned
527 |  | 34579 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-05-14 | 45426.2153 | 2024-05-14 | 45426.2903 | 0.018048 | 0.00026678 | 167 | 11298 | Planned | Planned
528 |  | 34580 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-14 | 45426.3333 | 2024-05-14 | 45426.6319 | 0.0054953 | 1.2779e-05 | 8 | 3440 | Planned | Planned
529 |  | 34582 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-05-14 | 45426.375 | 2024-05-14 | 45426.6458 | 0.001246 | 3.195e-06 | 2 | 780 | Planned | Planned
530 |  | 34583 | MCEN K01 - K01 MANGERE BRIDGE | Auckland | MCEN K01 | 2024-05-14 | 45426.4215 | 2024-05-14 | 45426.7181 | 0.077079 | 0.00018051 | 113 | 48251 | Planned | Planned
531 |  | 34584 | HOWI K16 - K16 PAKURANGA RD (497) | Auckland | HOWI K16 | 2024-05-14 | 45426.9583 | 2024-05-15 | 45427.0403 | 0.0028275 | 2.3962e-05 | 15 | 1770 | Planned | Planned
532 |  | 34586 | WEST K09 - K09 TELSTRA SATURN | Auckland | WEST K09 | 2024-05-15 | 45427.0833 | 2024-05-15 | 45427.1736 | 0.00083068 | 6.389e-06 | 4 | 520 | Planned | Planned
533 |  | 34587 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-05-15 | 45427.1389 | 2024-05-15 | 45427.6931 | 0.048288 | 8.1472e-05 | 51 | 30228 | Unplanned | Cause unknown
534 |  | 34588 | MEAS K12 - K12 MASSEY RD | Auckland | MEAS K12 | 2024-05-15 | 45427.2111 | 2024-05-15 | 45427.2604 | 0.043211 | 0.0017061 | 1068 | 27050 | Unplanned | Cause unknown
535 |  | 34590 | ONEH K01 - K01 - PAYNES LANE | Auckland | ONEH K01 | 2024-05-15 | 45427.3833 | 2024-05-15 | 45427.5785 | 0.085288 | 0.00030352 | 190 | 53390 | Planned | Planned
536 |  | 34591 | FBSH K05 - K05 WISTERIA LANE | Auckland | FBSH K05 | 2024-05-15 | 45427.4271 | 2024-05-15 | 45427.7639 | 0.0030991 | 6.389e-06 | 4 | 1940 | Planned | Planned
537 |  | 34592 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-05-15 | 45427.2667 | 2024-05-15 | 45427.3333 | 0.0024537 | 2.5557e-05 | 16 | 1536 | Unplanned | Cause unknown
538 |  | 34593 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-15 | 45427.3493 | 2024-05-15 | 45427.6507 | 0.054077 | 0.00012459 | 78 | 33852 | Planned | Planned
539 |  | 34594 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-05-15 | 45427.4403 | 2024-05-15 | 45427.6021 | 0.00037221 | 1.597e-06 | 1 | 233 | Unplanned | Third party interference
540 |  | 34595 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-05-15 | 45427.5486 | 2024-05-15 | 45427.6146 | 0.0015176 | 1.5974e-05 | 10 | 950 | Unplanned | Defective equipment
541 |  | 34596 | ORAK K04 - K04 HAWERA RD | Auckland | ORAK K04 | 2024-05-15 | 45427.7042 | 2024-05-16 | 45428.159 | 0.41731 | 0.002155 | 1022 | 261234 | Unplanned | Defective equipment
542 |  | 34596 | ORAK K04 - K04 HAWERA RD | Auckland | ORAK K11 | 2024-05-15 | 45427.7042 | 2024-05-16 | 45428.159 | 0.086213 | 0.0042572 | 828 | 53969 | Unplanned | Defective equipment
543 |  | 34597 | WEST K13 - K13 MAINLAND PRODUCTS | Auckland | WEST K13 | 2024-05-15 | 45427.6729 | 2024-05-15 | 45427.9028 | 0.00045208 | 3.196e-06 | 1 | 283 | Unplanned | Defective equipment
544 |  | 34598 | FREE K19 - K19 131 WELLINGTON ST | Auckland | FREE K64 | 2024-05-15 | 45427.9583 | 2024-05-16 | 45428.0312 | 0.0031869 | 3.0352e-05 | 19 | 1995 | Planned | Planned
545 |  | 34599 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2024-05-16 | 45428.0833 | 2024-05-16 | 45428.1597 | 0.0056231 | 5.1119e-05 | 32 | 3520 | Planned | Planned
546 |  | 34600 | MNAB K33 - K33 GAVIN STREET EAST | Auckland | MNAB K33 | 2024-05-16 | 45428.2083 | 2024-05-17 | 45429.2424 | 0.059106 | 0.0011821 | 370 | 37000 | Planned | Planned
547 |  | 34601 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-16 | 45428.2229 | 2024-05-16 | 45428.316 | 0.045909 | 0.00063739 | 399 | 28739 | Unplanned | Third party interference
548 |  | 34602 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-05-16 | 45428.2083 | 2024-05-16 | 45428.2882 | 0.029197 | 0.00026676 | 167 | 18277 | Planned | Planned
549 |  | 34603 | ORAK K02 - K02 WATERCARE #1 & HAWERA RD | Auckland | ORAK K02 | 2024-05-15 | 45427.641 | 2024-05-15 | 45427.8222 | 0 | 0 | 0 | 0 | Unplanned | Cause unknown
550 |  | 34604 | WSWA K08 - K08 COMMODORE DRIVE | Auckland | WSWA K08 | 2024-05-16 | 45428.3444 | 2024-05-16 | 45428.6792 | 0.032339 | 6.7093e-05 | 42 | 20244 | Planned | Planned
551 |  | 34605 | NSBT115 - N3686 H02 - BIG OMAHA H02 (115) | Northern | WARK K12 | 2024-05-16 | 45428.334 | 2024-05-16 | 45428.634 | 0.0020703 | 4.791e-06 | 3 | 1296 | Planned | Planned
552 |  | 34606 | CARB K13 - K13 PANAMA RD | Auckland | CARB K13 | 2024-05-16 | 45428.3514 | 2024-05-16 | 45428.5687 | 0.21199 | 0.00091535 | 573 | 132702 | Unplanned | Vegetation
553 |  | 34607 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-05-16 | 45428.375 | 2024-05-16 | 45428.6181 | 0.019732 | 0.00030671 | 128 | 12352 | Planned | Planned
554 |  | 34608 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-16 | 45428.3785 | 2024-05-16 | 45428.3958 | 0.00071886 | 2.8754e-05 | 18 | 450 | Planned | Planned
555 |  | 34609 | HPOI K04 - K04 MAPOU RD | Northern | HPOI K04 | 2024-05-16 | 45428.3764 | 2024-05-16 | 45428.6931 | 0.20396 | 0.00044729 | 280 | 127680 | Planned | Planned
556 |  | 34610 | HOBV K04 - K04 ELIZABETH DR | Northern | HOBV K04 | 2024-05-16 | 45428.375 | 2024-05-16 | 45428.6493 | 0.063731 | 0.00016134 | 101 | 39895 | Planned | Planned
557 |  | 34611 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-16 | 45428.434 | 2024-05-16 | 45428.6465 | 0.038128 | 0.0001246 | 78 | 23868 | Planned | Planned
558 |  | 34612 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-16 | 45428.3757 | 2024-05-16 | 45428.4306 | 0.0003786 | 4.792e-06 | 3 | 237 | Planned | Planned
559 |  | 34613 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-16 | 45428.441 | 2024-05-16 | 45428.4514 | 0.00055112 | 3.6742e-05 | 23 | 345 | Planned | Planned
560 |  | 34614 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-05-16 | 45428.3993 | 2024-05-16 | 45428.4771 | 3.8339e-05 | 6.39e-06 | 2 | 24 | Unplanned | Other Cause | Outage caused by Tap Operation
561 |  | 34615 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-05-16 | 45428.5125 | 2024-05-16 | 45428.5542 | 0.020895 | 0.00034825 | 218 | 13080 | Unplanned | Vegetation
562 |  | 34616 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-16 | 45428.5243 | 2024-05-16 | 45428.5347 | 4.7924e-05 | 3.195e-06 | 2 | 30 | Planned | Planned
563 |  | 34620 | WEST K13 - K13 MAINLAND PRODUCTS | Auckland | WEST K13 | 2024-05-16 | 45428.2549 | 2024-05-16 | 45428.5507 | 0.00068052 | 1.597e-06 | 1 | 426 | Unplanned | Defective equipment
564 |  | 34622 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-16 | 45428.5868 | 2024-05-16 | 45428.5972 | 0.00057509 | 3.8339e-05 | 24 | 360 | Planned | Planned
565 |  | 34623 | HOBV K11 - K11 TRIG RD +LS | Northern | HOBV K11 | 2024-05-16 | 45428.6556 | 2024-05-16 | 45428.7903 | 0.022933 | 0.00011821 | 74 | 14356 | Unplanned | Defective equipment
566 |  | 34624 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-16 | 45428.5944 | 2024-05-16 | 45428.6701 | 0.0057461 | 5.2714e-05 | 33 | 3597 | Unplanned | Cause unknown
567 |  | 34625 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-16 | 45428.6806 | 2024-05-16 | 45428.6875 | 0.039873 | 0.0039872 | 2496 | 24960 | Unplanned | Human error
568 |  | 34626 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-05-16 | 45428.5104 | 2024-05-16 | 45428.5799 | 0.00031949 | 3.195e-06 | 2 | 200 | Unplanned | Cause unknown
569 |  | 34627 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-16 | 45428.9583 | 2024-05-17 | 45429.0451 | 0.00039936 | 3.195e-06 | 2 | 250 | Planned | Planned
570 |  | 34628 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-17 | 45429.0833 | 2024-05-17 | 45429.1458 | 0.0010064 | 1.1181e-05 | 7 | 630 | Planned | Planned
571 |  | 34629 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-05-17 | 45429.334 | 2024-05-17 | 45429.6528 | 0.013931 | 3.0351e-05 | 19 | 8721 | Planned | Planned
572 |  | 34630 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-17 | 45429.3549 | 2024-05-17 | 45429.6174 | 0.046496 | 0.000123 | 77 | 29106 | Planned | Planned
573 |  | 34631 | HVAL K05 - K05 BORDER RD | Northern | HVAL K05 | 2024-05-17 | 45429.3549 | 2024-05-17 | 45429.7326 | 0.29807 | 0.00054793 | 343 | 186592 | Planned | Planned
574 |  | 34632 | WSWA K17 - K17 RICHARDSON RD O/H LINE WEST | Auckland | WSWA K17 | 2024-05-17 | 45429.3965 | 2024-05-17 | 45429.6201 | 0.098761 | 0.00030671 | 192 | 61824 | Planned | Planned
575 |  | 34633 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-17 | 45429.4618 | 2024-05-17 | 45429.7833 | 0.0022189 | 4.792e-06 | 3 | 1389 | Planned | Planned
576 |  | 34634 | WAIM K05 - K05 MURIWAI | Northern | WAIM K08 | 2024-05-17 | 45429.7396 | 2024-05-17 | 45429.8042 | 0.0068339 | 7.3477e-05 | 46 | 4278 | Unplanned | Defective equipment
577 |  | 34635 | MNAB K02 - K02 GAVIN ST WEST | Auckland | MNAB K02 | 2024-05-18 | 45430 | 2024-05-18 | 45430.2646 | 0.017042 | 4.4729e-05 | 28 | 10668 | Planned | Planned
578 |  | 34637 | BRIC K04 - K04 LINKS RD | Northern | BRIC K04 | 2024-05-18 | 45430.334 | 2024-05-18 | 45430.4236 | 0.0074186 | 5.7509e-05 | 36 | 4644 | Planned | Planned
579 |  | 34638 | BROW K04 - K04 NORTHCROSS | Northern | BROW K04 | 2024-05-18 | 45430.3576 | 2024-05-18 | 45430.7292 | 0.21504 | 0.00040575 | 254 | 134615 | Planned | Planned
580 |  | 34639 | GULF K05 - K05 ALEC CRAIG WAY | Northern | GULF K05 | 2024-05-18 | 45430.6465 | 2024-05-18 | 45430.7215 | 0.056959 | 0.0011374 | 712 | 35656 | Unplanned | Defective equipment
581 |  | 34640 | MKAU K09 - K09 CAVENDISH CENTRE | Auckland | MKAU K09 | 2024-05-18 | 45430.8542 | 2024-05-19 | 45431.2264 | 0.00019489 | 6.39e-06 | 4 | 122 | Planned | Planned
582 |  | 34642 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-19 | 45431.3819 | 2024-05-19 | 45431.6458 | 0.069342 | 0.0003227 | 202 | 43408 | Unplanned | Third party interference
583 |  | 34643 | RANU K09 - K09 ALIDADE PLACE | Northern | RANU K09 | 2024-05-19 | 45431.4681 | 2024-05-19 | 45431.575 | 0.10505 | 0.00068211 | 427 | 65758 | Unplanned | Third party interference
584 |  | 34644 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-19 | 45431.7799 | 2024-05-19 | 45431.7861 | 7.1886e-05 | 7.987e-06 | 5 | 45 | Unplanned | Other Cause | Outage caused by Tap Operation
585 |  | 34645 | MKAU K09 - K09 CAVENDISH CENTRE | Auckland | MKAU K09 | 2024-05-19 | 45431.8125 | 2024-05-19 | 45431.8486 | 0.00011182 | 6.39e-06 | 4 | 70 | Planned | Planned
586 |  | 34646 | SYLV K03 - K03 COCA COLA No.1 | Auckland | SYLV K03 | 2024-05-19 | 45431.834 | 2024-05-20 | 45432.0222 | 0.00019329 | 1.597e-06 | 1 | 121 | Planned | Planned
587 |  | 34646 | SYLV K03 - K03 COCA COLA No.1 | Auckland | SYLV K11 | 2024-05-19 | 45431.834 | 2024-05-20 | 45432.0222 | 0.00023962 | 1.597e-06 | 1 | 150 | Planned | Planned
588 |  | 34647 | SHEL K06 - K06 RIDDELL RD EAST | Auckland | SHEL K06 | 2024-05-20 | 45432.1465 | 2024-05-20 | 45432.2146 | 0.0073579 | 7.5081e-05 | 47 | 4606 | Planned | Planned
589 |  | 34648 | WARK K08 - K08 GOLF | Northern | WARK K08 | 2024-05-20 | 45432.2875 | 2024-05-20 | 45432.6687 | 0.023679 | 4.3131e-05 | 27 | 14823 | Unplanned | Wildlife
590 |  | 34649 | SJOH K11 - K11 COLLEGE RD | Auckland | SJOH K11 | 2024-05-20 | 45432.3979 | 2024-05-20 | 45432.566 | 0.01701 | 7.0288e-05 | 44 | 10648 | Planned | Planned
591 |  | 34650 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-05-20 | 45432.4201 | 2024-05-20 | 45432.6181 | 0.2158 | 0.0007572 | 474 | 135090 | Planned | Planned
592 |  | 34651 | HCRE K02 - K02 FOWLER STREET | Northern | HCRE K02 | 2024-05-20 | 45432.5028 | 2024-05-20 | 45432.5785 | 0.057809 | 0.00053036 | 332 | 36188 | Planned | Planned
593 |  | 34653 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-20 | 45432.6965 | 2024-05-20 | 45432.7743 | 0.042413 | 0.00064212 | 402 | 26550 | Unplanned | Cause unknown
594 |  | 34654 | BMON K03 - K03 CENTRAL | Northern | BMON K03 | 2024-05-20 | 45432.834 | 2024-05-20 | 45432.9292 | 0.053619 | 0.00039138 | 245 | 33565 | Planned | Planned
595 |  | 34655 | ONEH K02 - K02 - GALWAY ST | Auckland | ONEH K02 | 2024-05-20 | 45432.8757 | 2024-05-21 | 45433.1396 | 0.0030352 | 7.987e-06 | 5 | 1900 | Planned | Planned
596 |  | 34656 | BLMN K01 - K01 ISLAND BAY | Northern | BLMN K01 | 2024-05-20 | 45432.8944 | 2024-05-20 | 45432.9132 | 0.0045719 | 0.00016933 | 106 | 2862 | Unplanned | Defective equipment
597 |  | 34661 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-20 | 45432.966 | 2024-05-21 | 45433.0167 | 0.0048978 | 6.7091e-05 | 42 | 3066 | Unplanned | Cause unknown
598 |  | 34662 | BAIR K03 - K03 BAIRDS ROAD WEST VIA LS | Auckland | BAIR K03 | 2024-05-20 | 45432.9583 | 2024-05-21 | 45433.0299 | 0.03373 | 0.00032748 | 205 | 21115 | Planned | Planned
599 |  | 34663 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-05-20 | 45432.9583 | 2024-05-21 | 45433.0486 | 0.04278 | 0.00032908 | 206 | 26780 | Planned | Planned
600 |  | 34665 | HANS K05 - K05 KRAFT FOODS | Auckland | HANS K05 | 2024-05-20 | 45432.9792 | 2024-05-21 | 45433.1701 | 0.0070288 | 2.5559e-05 | 16 | 4400 | Planned | Planned
601 |  | 34666 | MKIN K11 - K11 THE AVENUE | Northern | MKIN K11 | 2024-05-20 | 45432.9569 | 2024-05-21 | 45433.091 | 0.02189 | 0.00011342 | 71 | 13703 | Unplanned | Defective equipment
602 |  | 34667 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-05-20 | 45432.9285 | 2024-05-21 | 45433.8056 | 0.0020176 | 1.597e-06 | 1 | 1263 | Unplanned | Third party interference
603 |  | 34668 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-20 | 45432.9688 | 2024-05-21 | 45433.2722 | 0.018848 | 4.3132e-05 | 27 | 11799 | Unplanned | Vegetation
604 |  | 34669 | HCRE K02 - K02 FOWLER STREET | Northern | HCRE K02 | 2024-05-21 | 45433.0243 | 2024-05-21 | 45433.0694 | 0.0017652 | 2.7157e-05 | 17 | 1105 | Unplanned | Cause unknown
605 |  | 34670 | SHOW K05 - K05 LITTEN RD | Auckland | SHOW K05 | 2024-05-21 | 45433.0833 | 2024-05-21 | 45433.1736 | 0.017444 | 0.00013419 | 84 | 10920 | Planned | Planned
606 |  | 34671 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-05-21 | 45433.0667 | 2024-05-21 | 45433.1889 | 0.050192 | 0.00077478 | 485 | 31420 | Unplanned | Vegetation
607 |  | 34672 | ASBT273 - TP TAKANINI 2272 - MARAETAI H06 | Auckland | MARA K04 | 2024-05-21 | 45433.0854 | 2024-05-21 | 45433.1653 | 0.021122 | 0.00041213 | 258 | 13222 | Unplanned | Vegetation
608 |  | 34673 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-05-21 | 45433.0542 | 2024-05-21 | 45433.2465 | 0.00088499 | 3.195e-06 | 2 | 554 | Unplanned | Vegetation
609 |  | 34674 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-05-21 | 45433.1965 | 2024-05-21 | 45433.241 | 0.0022492 | 3.5143e-05 | 22 | 1408 | Unplanned | Cause unknown
610 |  | 34676 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K03 | 2024-05-21 | 45433.3542 | 2024-05-21 | 45433.7125 | 0.023002 | 4.7929e-05 | 30 | 14399 | Planned | Planned
611 |  | 34676 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-21 | 45433.3542 | 2024-05-21 | 45433.7125 | 0.0030032 | 6.385e-06 | 4 | 1880 | Planned | Planned
612 |  | 34677 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-05-21 | 45433.3431 | 2024-05-21 | 45433.6701 | 0.0030096 | 6.389e-06 | 4 | 1884 | Planned | Planned
613 |  | 34678 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-21 | 45433.375 | 2024-05-21 | 45433.3819 | 0.00062301 | 6.2301e-05 | 39 | 390 | Planned | Planned
614 |  | 34679 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-05-21 | 45433.3333 | 2024-05-21 | 45433.7167 | 0.19664 | 0.00035623 | 223 | 123096 | Planned | Planned
615 |  | 34680 | AVON K05 - K05 BLOCKHOUSE BAY RD. NORTH | Auckland | AVON K05 | 2024-05-21 | 45433.4042 | 2024-05-21 | 45433.7333 | 0.15143 | 0.00032428 | 203 | 94796 | Planned | Planned
616 |  | 34681 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-21 | 45433.4375 | 2024-05-21 | 45433.441 | 0.00031949 | 6.3898e-05 | 40 | 200 | Planned | Planned
617 |  | 34682 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-21 | 45433.2847 | 2024-05-21 | 45433.5431 | 0.00059426 | 1.597e-06 | 1 | 372 | Unplanned | Cause unknown
618 |  | 34683 | GULF K15 - K15 EVERARD AVE + LS | Northern | GULF K15 | 2024-05-21 | 45433.5236 | 2024-05-21 | 45433.5611 | 0.0015527 | 2.8754e-05 | 18 | 972 | Unplanned | Defective equipment
619 |  | 34686 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-21 | 45433.5208 | 2024-05-21 | 45433.5278 | 0.00031949 | 3.1949e-05 | 20 | 200 | Planned | Planned
620 |  | 34687 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-21 | 45433.5833 | 2024-05-21 | 45433.5889 | 0.00057509 | 7.1886e-05 | 45 | 360 | Planned | Planned
621 |  | 34689 | ONEH K05 - K05 - VICTORIA ST | Auckland | ONEH K05 | 2024-05-22 | 45434.0833 | 2024-05-22 | 45434.1618 | 0.0045128 | 3.9936e-05 | 25 | 2825 | Planned | Planned
622 |  | 34691 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-05-22 | 45434.3375 | 2024-05-22 | 45434.6736 | 0.24046 | 0.0004968 | 311 | 150524 | Planned | Planned
623 |  | 34692 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-05-22 | 45434.3764 | 2024-05-22 | 45434.6861 | 0.11328 | 0.00025398 | 159 | 70914 | Planned | Planned
624 |  | 34693 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-05-22 | 45434.3764 | 2024-05-22 | 45434.7354 | 0.00082589 | 1.597e-06 | 1 | 517 | Planned | Planned
625 |  | 34694 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-22 | 45434.3819 | 2024-05-22 | 45434.6826 | 0.025652 | 6.5492e-05 | 41 | 16058 | Planned | Planned
626 |  | 34695 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-05-22 | 45434.4167 | 2024-05-22 | 45434.4736 | 0.015457 | 0.0001885 | 118 | 9676 | Planned | Planned
627 |  | 34696 | NEWM K04 - K04 MAHURU ST | Auckland | NEWM K04 | 2024-05-22 | 45434.6389 | 2024-05-22 | 45434.7812 | 0.0029186 | 0.00010064 | 63 | 1827 | Unplanned | Defective equipment
628 |  | 34697 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-05-22 | 45434.8208 | 2024-05-22 | 45434.8354 | 3.3547e-05 | 1.597e-06 | 1 | 21 | Unplanned | Defective equipment
629 |  | 34698 | ROSE K09 - K09 ALUMINIUM ANODISERS | Auckland | ROSE K09 | 2024-05-22 | 45434.9583 | 2024-05-23 | 45435.0389 | 0.0027796 | 2.3961e-05 | 15 | 1740 | Planned | Planned
630 |  | 34699 | MCEN K11 - K11 MAHUNGA DRIVE | Auckland | MCEN K11 | 2024-05-23 | 45435.0833 | 2024-05-23 | 45435.1646 | 0.0029904 | 2.5559e-05 | 16 | 1872 | Planned | Planned
631 |  | 34700 | SYLV K02 - K02 MT WELLINGTON HWY VIA RMU | Auckland | SYLV K02 | 2024-05-23 | 45435.209 | 2024-05-23 | 45435.2583 | 0.080982 | 0.0011406 | 714 | 50694 | Planned | Planned
632 |  | 34701 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-05-23 | 45435.3819 | 2024-05-23 | 45435.7188 | 0.12164 | 0.0002508 | 157 | 76145 | Planned | Planned
633 |  | 34702 | RDAL K11 - K11 HUGH GREEN DR | Northern | RDAL K11 | 2024-05-23 | 45435.375 | 2024-05-23 | 45435.7264 | 0.0016166 | 3.195e-06 | 2 | 1012 | Planned | Planned
634 |  | 34703 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-05-23 | 45435.3979 | 2024-05-23 | 45435.5153 | 0.020788 | 0.00012301 | 77 | 13013 | Planned | Planned
635 |  | 34704 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-05-23 | 45435.3576 | 2024-05-23 | 45435.6528 | 0.00067892 | 1.597e-06 | 1 | 425 | Planned | Planned
636 |  | 34705 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-05-23 | 45435.3799 | 2024-05-23 | 45435.7056 | 0.020229 | 4.313e-05 | 27 | 12663 | Planned | Planned
637 |  | 34706 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-05-23 | 45435.3868 | 2024-05-23 | 45435.4014 | 0.00013419 | 6.39e-06 | 4 | 84 | Unplanned | Defective equipment
638 |  | 34707 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-05-23 | 45435.5125 | 2024-05-24 | 45436.5938 | 0.0024872 | 1.597e-06 | 1 | 1557 | Unplanned | Defective equipment
639 |  | 34709 | TATA K02 - K02 TAIKATA RD | Northern | TATA K02 | 2024-05-23 | 45435.8292 | 2024-05-23 | 45435.8424 | 0.025162 | 0.0013243 | 829 | 15751 | Unplanned | Defective equipment
640 |  | 34709 | TATA K02 - K02 TAIKATA RD | Northern | TATA K11 | 2024-05-23 | 45435.8292 | 2024-05-23 | 45435.8424 | 0.00053036 | 0.00013259 | 83 | 332 | Unplanned | Defective equipment
641 |  | 34710 | MANU K03 - K03 COXHEAD RD | Auckland | MANU K03 | 2024-05-23 | 45435.8764 | 2024-05-24 | 45436.2465 | 0.07663 | 0.00014377 | 90 | 47970 | Planned | Planned
642 |  | 34711 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-23 | 45435.8438 | 2024-05-23 | 45435.9792 | 0.0015575 | 7.987e-06 | 5 | 975 | Unplanned | Cause unknown
643 |  | 34712 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-05-23 | 45435.9792 | 2024-05-24 | 45436.1549 | 0.030312 | 0.0001198 | 75 | 18975 | Planned | Planned
644 |  | 34713 | SYLV K02 - K02 MT WELLINGTON HWY VIA RMU | Auckland | SYLV K02 | 2024-05-24 | 45436.2597 | 2024-05-24 | 45436.284 | 0.032149 | 0.00091854 | 575 | 20125 | Planned | Planned
645 |  | 34714 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-24 | 45436.3583 | 2024-05-24 | 45436.6847 | 0.042045 | 8.9451e-05 | 56 | 26320 | Planned | Planned
646 |  | 34715 | WOOD K01 - K01 LINCOLN ROAD | Northern | WOOD K01 | 2024-05-24 | 45436.3931 | 2024-05-24 | 45436.6785 | 0.12212 | 0.00029713 | 186 | 76446 | Planned | Planned
647 |  | 34716 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-24 | 45436.375 | 2024-05-24 | 45436.384 | 2.0767e-05 | 1.597e-06 | 1 | 13 | Planned | Planned
648 |  | 34717 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-24 | 45436.4375 | 2024-05-24 | 45436.4472 | 0.00064857 | 4.6326e-05 | 29 | 406 | Planned | Planned
649 |  | 34718 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-24 | 45436.5417 | 2024-05-24 | 45436.5556 | 0.00025559 | 1.278e-05 | 8 | 160 | Planned | Planned
650 |  | 34719 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-24 | 45436.6042 | 2024-05-24 | 45436.6146 | 2.3962e-05 | 1.597e-06 | 1 | 15 | Planned | Planned
651 |  | 34720 | SJOH K11 - K11 COLLEGE RD | Auckland | SJOH K11 | 2024-05-24 | 45436.3979 | 2024-05-24 | 45436.5771 | 0.018134 | 7.0288e-05 | 44 | 11352 | Planned | Planned
652 |  | 34722 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-05-24 | 45436.4167 | 2024-05-24 | 45436.6979 | 0.0012939 | 3.195e-06 | 2 | 810 | Planned | Planned
653 |  | 34723 | HPOI K12 - K12 HOBSONVILLE RD | Northern | HPOI K12 | 2024-05-24 | 45436.9375 | 2024-05-25 | 45437.2201 | 0.0032508 | 7.987e-06 | 5 | 2035 | Planned | Planned
654 |  | 34724 | SUNS K04 - K04 MAXWELTON DRIVE | Northern | SUNS K04 | 2024-05-25 | 45437.375 | 2024-05-25 | 45437.7417 | 0.0025304 | 4.792e-06 | 3 | 1584 | Planned | Planned
655 |  | 34725 | FORR K06 - K06 CHANNEL VIEW | Northern | FORR K06 | 2024-05-25 | 45437.3785 | 2024-05-25 | 45437.509 | 0.015316 | 8.147e-05 | 51 | 9588 | Planned | Planned
656 |  | 34726 | MALB K20 - K20 FOWLER AVE | Auckland | MALB K20 | 2024-05-25 | 45437.3993 | 2024-05-25 | 45437.6479 | 0.16585 | 0.00046326 | 290 | 103820 | Planned | Planned
657 |  | 34727 | TATA K10 - K10 FLANSHAW RD | Northern | TATA K10 | 2024-05-25 | 45437.4194 | 2024-05-25 | 45437.5729 | 0.013062 | 5.9106e-05 | 37 | 8177 | Planned | Planned
658 |  | 34728 | RIVE K11 - K11 CARTERS MILL | Northern | RIVE K11 | 2024-05-25 | 45437.3292 | 2024-05-25 | 45437.4826 | 0.00035304 | 1.597e-06 | 1 | 221 | Unplanned | Vegetation
659 |  | 34729 | TATA K11 - K11 YEOVIL ROAD | Northern | TATA K11 | 2024-05-25 | 45437.6271 | 2024-05-25 | 45437.9549 | 0.3033 | 0.00065337 | 409 | 189865 | Planned | Planned
660 |  | 34730 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-25 | 45437.5597 | 2024-05-25 | 45437.6674 | 0.00074282 | 4.792e-06 | 3 | 465 | Unplanned | Vegetation
661 |  | 34731 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-05-25 | 45437.7826 | 2024-05-25 | 45437.8715 | 0.0008179 | 6.39e-06 | 4 | 512 | Unplanned | Cause unknown
662 |  | 34732 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-25 | 45437.8812 | 2024-05-26 | 45438.4201 | 0.099491 | 0.00080834 | 206 | 62281 | Unplanned | Vegetation
663 |  | 34733 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-05-26 | 45438.2493 | 2024-05-26 | 45438.7903 | 0.18942 | 0.00054791 | 236 | 118574 | Unplanned | Vegetation
664 |  | 34734 | TATA K01 - K01 WINSTON PL | Northern | TATA K01 | 2024-05-26 | 45438.3333 | 2024-05-26 | 45438.7201 | 0.029363 | 5.2716e-05 | 33 | 18381 | Planned | Planned
665 |  | 34736 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-26 | 45438.5042 | 2024-05-26 | 45438.8778 | 0.11306 | 0.0003291 | 206 | 70778 | Unplanned | Third party interference
666 |  | 34737 | SHOW K02 - K02 GILLET PL | Auckland | SHOW K02 | 2024-05-26 | 45438.3562 | 2024-05-26 | 45438.5792 | 0.056002 | 0.00040256 | 163 | 35057 | Unplanned | Cause unknown
667 |  | 34739 | WIRI K15 - K15 KEITH HAY DR | Auckland | WIRI K15 | 2024-05-26 | 45438.9167 | 2024-05-27 | 45439.2465 | 0.06298 | 0.00013259 | 83 | 39425 | Planned | Planned
668 |  | 34740 | ONEH K05 - K05 - VICTORIA ST | Auckland | ONEH K05 | 2024-05-26 | 45438.9375 | 2024-05-27 | 45439.0167 | 0.0014569 | 1.278e-05 | 8 | 912 | Planned | Planned
669 |  | 34741 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-05-27 | 45439.0625 | 2024-05-27 | 45439.1604 | 0.034012 | 0.00024122 | 151 | 21291 | Planned | Planned
670 |  | 34744 | SUNS K05 - K05 MEADOWOOD DRIVE | Northern | SUNS K05 | 2024-05-27 | 45439.5833 | 2024-05-27 | 45439.6104 | 0.0011837 | 3.0352e-05 | 19 | 741 | Planned | Planned
671 |  | 34745 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-05-27 | 45439.6264 | 2024-05-27 | 45439.7778 | 0.001393 | 6.39e-06 | 4 | 872 | Unplanned | Defective equipment
672 |  | 34747 | VICT K24 - K24 BROOKE BUILDING VIA LS | Auckland | VICT K24 | 2024-05-27 | 45439.8757 | 2024-05-28 | 45440.1729 | 0.015725 | 3.6742e-05 | 23 | 9844 | Planned | Planned
673 |  | 34748 | MCEN K12 - K12 ROBERTSON ROAD SOUTH | Auckland | MCEN K12 | 2024-05-27 | 45439.9583 | 2024-05-28 | 45440.1806 | 0.18709 | 0.00058467 | 366 | 117120 | Planned | Planned
674 |  | 34750 | MKAU K22 - K22 MCDONALDS | Auckland | MKAU K23 | 2024-05-28 | 45440.0208 | 2024-05-28 | 45440.1764 | 0.00035783 | 1.597e-06 | 1 | 224 | Planned | Planned
675 |  | 34751 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-05-28 | 45440.2569 | 2024-05-28 | 45440.7806 | 0.1273 | 0.00033227 | 189 | 79686 | Planned | Planned
676 |  | 34752 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-05-28 | 45440.3375 | 2024-05-28 | 45440.6771 | 0.0062493 | 1.278e-05 | 8 | 3912 | Planned | Planned
677 |  | 34754 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-28 | 45440.3611 | 2024-05-28 | 45440.6549 | 0.00067572 | 1.597e-06 | 1 | 423 | Planned | Planned
678 |  | 34756 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-28 | 45440.3333 | 2024-05-28 | 45440.691 | 0.0041135 | 7.987e-06 | 5 | 2575 | Planned | Planned
679 |  | 34757 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-05-28 | 45440.3958 | 2024-05-28 | 45440.484 | 0.019882 | 0.00015655 | 98 | 12446 | Planned | Planned
680 |  | 34758 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-28 | 45440.375 | 2024-05-28 | 45440.4139 | 0.00035783 | 6.39e-06 | 4 | 224 | Planned | Planned
681 |  | 34759 | BUSH K08 - K08 UNITY DR | Northern | BUSH K08 | 2024-05-28 | 45440.3924 | 2024-05-29 | 45441.1833 | 0.054585 | 4.7924e-05 | 30 | 34170 | Unplanned | Defective equipment
682 |  | 34760 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-28 | 45440.4097 | 2024-05-28 | 45440.5139 | 0.00023962 | 1.597e-06 | 1 | 150 | Planned | Planned
683 |  | 34761 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-05-28 | 45440.4396 | 2024-05-28 | 45440.6042 | 0.005679 | 2.3962e-05 | 15 | 3555 | Planned | Planned
684 |  | 34762 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-28 | 45440.4375 | 2024-05-28 | 45440.4778 | 0.00055592 | 9.585e-06 | 6 | 348 | Planned | Planned
685 |  | 34763 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-05-28 | 45440.4382 | 2024-05-28 | 45440.4951 | 0.00013099 | 1.597e-06 | 1 | 82 | Unplanned | Wildlife
686 |  | 34764 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2024-05-28 | 45440.5451 | 2024-05-28 | 45440.6347 | 0.031842 | 0.00080991 | 507 | 19933 | Unplanned | Defective equipment
687 |  | 34765 | BRIC K05 - K05 PORTAGE RD | Northern | BRIC K05 | 2024-05-28 | 45440.5451 | 2024-05-28 | 45440.6813 | 0.0003131 | 1.597e-06 | 1 | 196 | Unplanned | Cause unknown
688 |  | 34766 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-28 | 45440.5208 | 2024-05-28 | 45440.5618 | 0.0001885 | 3.195e-06 | 2 | 118 | Planned | Planned
689 |  | 34768 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-05-28 | 45440.65 | 2024-05-29 | 45441.1181 | 0.022612 | 0.00029714 | 125 | 14155 | Unplanned | Third party interference
690 |  | 34769 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-05-28 | 45440.6993 | 2024-05-28 | 45440.7618 | 0.03393 | 0.00037699 | 236 | 21240 | Unplanned | Defective equipment
691 |  | 34770 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-28 | 45440.5833 | 2024-05-28 | 45440.6236 | 9.2653e-05 | 1.597e-06 | 1 | 58 | Planned | Planned
692 |  | 34772 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-28 | 45440.8681 | 2024-05-28 | 45440.9437 | 0.0019154 | 1.7572e-05 | 11 | 1199 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
693 |  | 34773 | ROSE K09 - K09 ALUMINIUM ANODISERS | Auckland | ROSE K09 | 2024-05-28 | 45440.9792 | 2024-05-29 | 45441.1319 | 0.0028115 | 1.278e-05 | 8 | 1760 | Planned | Planned
694 |  | 34774 | QUAY K23 - K23 SOFRANA HOUSE | Auckland | QUAY K23 | 2024-05-28 | 45440.9167 | 2024-05-29 | 45441.1833 | 0.034965 | 9.1055e-05 | 57 | 21888 | Planned | Planned
695 |  | 34775 | SUNS K05 - K05 MEADOWOOD DRIVE | Northern | SUNS K05 | 2024-05-29 | 45441.3333 | 2024-05-29 | 45441.3549 | 0.0009409 | 3.0352e-05 | 19 | 589 | Planned | Planned
696 |  | 34776 | WGAT K11 - K11 HOLMES | Northern | WGAT K11 | 2024-05-29 | 45441.3333 | 2024-05-30 | 45442.7458 | 0.078333 | 0.00029393 | 92 | 49036 | Planned | Planned
697 |  | 34777 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-05-29 | 45441.3368 | 2024-05-29 | 45441.6458 | 0.0099522 | 2.2364e-05 | 14 | 6230 | Planned | Planned
698 |  | 34778 | SWAN K03 - K03 HETHERINGTON | Northern | SWAN K03 | 2024-05-29 | 45441.3861 | 2024-05-29 | 45441.6438 | 0.060451 | 0.00016294 | 102 | 37842 | Planned | Planned
699 |  | 34787 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-05-29 | 45441.4201 | 2024-05-29 | 45441.4965 | 0.010368 | 9.4251e-05 | 59 | 6490 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
700 |  | 34788 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-05-29 | 45441.4278 | 2024-05-29 | 45441.4896 | 0.00099522 | 1.1182e-05 | 7 | 623 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
701 |  | 34790 | HCRE K02 - K02 FOWLER STREET | Northern | HCRE K02 | 2024-05-29 | 45441.4882 | 2024-05-29 | 45441.509 | 0.0008147 | 2.7157e-05 | 17 | 510 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
702 |  | 34791 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-05-29 | 45441.5146 | 2024-05-29 | 45441.6306 | 0.19307 | 0.001639 | 1026 | 120860 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
703 |  | 34792 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-29 | 45441.5028 | 2024-05-29 | 45441.559 | 0.065825 | 0.0010304 | 645 | 41206 | Unplanned | Other Cause | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
704 |  | 34793 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-05-29 | 45441.4389 | 2024-05-29 | 45441.5729 | 0.00098244 | 7.986e-06 | 5 | 615 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
705 |  | 34794 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-29 | 45441.4417 | 2024-05-29 | 45441.7569 | 0.016681 | 3.6738e-05 | 23 | 10442 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
706 |  | 34795 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-29 | 45441.4257 | 2024-05-29 | 45441.4979 | 0.00049841 | 4.792e-06 | 3 | 312 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
707 |  | 34796 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-05-29 | 45441.4542 | 2024-06-01 | 45444.6354 | 0.02769 | 2.8754e-05 | 9 | 17334 | Unplanned | Lightning | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
708 |  | 34797 | OREW K01 - K01 SAVOY RD | Northern | OREW K01 | 2024-05-29 | 45441.5403 | 2024-05-29 | 45441.941 | 0.20124 | 0.0023946 | 1499 | 125973 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
709 |  | 34798 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-05-29 | 45441.5507 | 2024-05-30 | 45442.7979 | 0.64813 | 0.00071887 | 236 | 405724 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
710 |  | 34799 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-05-29 | 45441.5604 | 2024-05-31 | 45443.691 | 0.31941 | 0.0013626 | 396 | 199949 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
711 |  | 34800 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-29 | 45441.5701 | 2024-05-30 | 45442.0174 | 0.24689 | 0.00046171 | 289 | 154551 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
712 |  | 34801 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-29 | 45441.5896 | 2024-05-29 | 45441.9729 | 0.3016 | 0.0010336 | 445 | 188802 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
713 |  | 34802 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-05-29 | 45441.6188 | 2024-05-29 | 45441.7472 | 0.042852 | 0.00023162 | 145 | 26825 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
714 |  | 34803 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2024-05-29 | 45441.6326 | 2024-05-30 | 45442.6944 | 0.11398 | 0.0040703 | 943 | 71352 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
715 |  | 34803 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K06 | 2024-05-29 | 45441.6326 | 2024-05-30 | 45442.6944 | 0.42809 | 0.00127 | 320 | 267979 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
716 |  | 34804 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-29 | 45441.6361 | 2024-05-31 | 45443.1389 | 0.25672 | 0.00025558 | 160 | 160706 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
717 |  | 34805 | TAKA K12 - K12 MILL RD | Auckland | FBSH K13 | 2024-05-29 | 45441.6368 | 2024-05-29 | 45441.8111 | 0.00021565 | 0.00021565 | 135 | 135 | Unplanned | Human error | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
718 |  | 34805 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-05-29 | 45441.6368 | 2024-05-29 | 45441.8111 | 0.051879 | 0.0025622 | 1604 | 32476 | Unplanned | Human error | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
719 |  | 34806 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-05-29 | 45441.6333 | 2024-05-29 | 45441.959 | 0.27121 | 0.00057825 | 362 | 169778 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
720 |  | 34807 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-29 | 45441.6382 | 2024-05-31 | 45443.9625 | 0.47983 | 0.001 | 313 | 300373 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
721 |  | 34808 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-29 | 45441.6465 | 2024-05-30 | 45442.7583 | 0.53238 | 0.00096489 | 399 | 333267 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
722 |  | 34809 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-05-29 | 45441.6806 | 2024-05-29 | 45441.8799 | 0.049015 | 0.00017414 | 109 | 30683 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
723 |  | 34810 | RIVE K09 - K09 KUMEU | Northern | RIVE K08 | 2024-05-29 | 45441.6806 | 2024-05-30 | 45442.3681 | 1.597e-06 | 1.597e-06 | 1 | 1 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
724 |  | 34810 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-05-29 | 45441.6806 | 2024-05-30 | 45442.3681 | 0.22165 | 0.00077314 | 484 | 138750 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
725 |  | 34810 | RIVE K09 - K09 KUMEU | Northern | WAIM K09 | 2024-05-29 | 45441.6806 | 2024-05-30 | 45442.3681 | 0.036023 | 0.0032748 | 2050 | 22550 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
726 |  | 34811 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-29 | 45441.6417 | 2024-05-29 | 45441.7778 | 0.13049 | 0.001623 | 732 | 81684 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
727 |  | 34812 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-29 | 45441.6875 | 2024-05-29 | 45441.8681 | 0.11507 | 0.00052878 | 331 | 72035 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
728 |  | 34813 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-29 | 45441.6924 | 2024-05-29 | 45441.8861 | 0.23101 | 0.0016981 | 1063 | 144611 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
729 |  | 34815 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-05-29 | 45441.7208 | 2024-05-30 | 45442.6222 | 0.89022 | 0.0029665 | 1857 | 557272 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
730 |  | 34817 | MKAU K12 - K12 LAMBIE DRIVE | Auckland | MKAU K12 | 2024-05-29 | 45441.7167 | 2024-05-29 | 45441.9375 | 0.22067 | 0.0026821 | 1679 | 138140 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
731 |  | 34818 | HOWI K06 - K06 BLEAKHOUSE RD | Auckland | HOWI K06 | 2024-05-29 | 45441.7243 | 2024-05-30 | 45442.0271 | 0.31804 | 0.0017764 | 1112 | 199092 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
732 |  | 34819 | TPAP K08 - K08 CHURCH ST WEST VIA LS | Auckland | TPAP K08 | 2024-05-29 | 45441.7444 | 2024-05-30 | 45442.7326 | 0.061376 | 4.3131e-05 | 27 | 38421 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
733 |  | 34821 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-05-29 | 45441.7396 | 2024-05-30 | 45442.5417 | 0.24131 | 0.00095371 | 597 | 151060 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
734 |  | 34822 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-29 | 45441.7701 | 2024-05-30 | 45442.6458 | 0.40878 | 0.0020734 | 952 | 255894 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
735 |  | 34823 | BAIR K10 - K10 BAIRDS ROAD EAST | Auckland | BAIR K10 | 2024-05-29 | 45441.7708 | 2024-05-30 | 45442.1854 | 0.56249 | 0.0013722 | 859 | 352113 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
736 |  | 34824 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-05-29 | 45441.7736 | 2024-05-30 | 45442.6062 | 0.1581 | 0.0002524 | 158 | 98970 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
737 |  | 34825 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-05-29 | 45441.6493 | 2024-05-29 | 45441.8889 | 0.0055112 | 1.5973e-05 | 10 | 3450 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
738 |  | 34826 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-05-29 | 45441.7771 | 2024-05-30 | 45442.1 | 0.15367 | 0.0018003 | 1127 | 96194 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
739 |  | 34826 | RANU K04 - K04 GLEN ROAD | Northern | TRIA K10 | 2024-05-29 | 45441.7771 | 2024-05-30 | 45442.1 | 0.058371 | 0.0013898 | 870 | 36540 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
740 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | CLEV R134 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.015887 | 0.00037384 | 117 | 9945 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
741 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | CLEV R140 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.14325 | 0.0032782 | 1026 | 89674 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
742 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | FBSH K13 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.0006901 | 0.00023003 | 144 | 432 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
743 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | MARA K01 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.33727 | 0.0078435 | 2455 | 211130 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
744 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | MARA K04 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.22845 | 0.0037173 | 979 | 143008 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
745 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | MARA K05 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.070751 | 0.0016454 | 515 | 44290 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
746 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | MARA K08 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.0061566 | 0.00013099 | 41 | 3854 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
747 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | MARA K10 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.032435 | 0.0006901 | 216 | 20304 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
748 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | MARA K11 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.02778 | 0.00059106 | 185 | 17390 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
749 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | WAIH K02 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.19069 | 0.003316 | 1038 | 119370 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
750 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | WAIH K03 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.27942 | 0.0048595 | 1521 | 174915 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
751 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | WAIH K05 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.33746 | 0.0062494 | 1956 | 211248 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
752 |  | 34827 | ASBT274A - TP TAKANINI 2192 - CLEVEDON H01 | Auckland | WAIH K06 | 2024-05-29 | 45441.7965 | 2024-05-29 | 45441.9062 | 0.20979 | 0.0038851 | 1216 | 131328 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
753 |  | 34828 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | HELE K04 | 2024-05-29 | 45441.7264 | 2024-05-30 | 45442.9944 | 0.00057188 | 0.00057188 | 358 | 358 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
754 |  | 34828 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-05-29 | 45441.7264 | 2024-05-30 | 45442.9944 | 0.44804 | 0.001465 | 739 | 280468 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
755 |  | 34829 | HANS K02 - K02 MASSEY RD NO.1 | Auckland | HANS K02 | 2024-05-29 | 45441.7965 | 2024-05-31 | 45443 | 0.89506 | 0.0017221 | 920 | 560302 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
756 |  | 34830 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-29 | 45441.7917 | 2024-05-29 | 45441.8229 | 0.0013658 | 3.035e-05 | 19 | 855 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
757 |  | 34831 | MWES K02 - K02 ORUARANGI RD | Auckland | MWES K02 | 2024-05-29 | 45441.8333 | 2024-05-30 | 45442.8549 | 0.076544 | 0.00021085 | 132 | 47916 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
758 |  | 34833 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-05-29 | 45441.8354 | 2024-05-30 | 45442.2396 | 0.78834 | 0.0079074 | 2716 | 493494 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
759 |  | 34834 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-05-29 | 45441.8083 | 2024-05-29 | 45441.9604 | 0.14106 | 0.00087064 | 545 | 88305 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
760 |  | 34835 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2024-05-29 | 45441.834 | 2024-05-29 | 45441.9694 | 0.12413 | 0.00086902 | 544 | 77706 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
761 |  | 34836 | MCEN K11 - K11 MAHUNGA DRIVE | Auckland | MCEN K11 | 2024-05-29 | 45441.8896 | 2024-05-30 | 45442.1965 | 0.077748 | 0.00043292 | 271 | 48670 | Unplanned | Human error | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
762 |  | 34837 | JAME K07 - K07 SPINELLA DRIVE | Northern | JAME K07 | 2024-05-29 | 45441.8097 | 2024-05-30 | 45442.1819 | 0.45956 | 0.0016582 | 1038 | 287682 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
763 |  | 34838 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-29 | 45441.8715 | 2024-05-30 | 45442.7139 | 0.1182 | 9.7436e-05 | 61 | 73993 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
764 |  | 34839 | HOBV K08 - K08 LUCKENS RD | Northern | HOBV K08 | 2024-05-29 | 45441.8375 | 2024-05-29 | 45441.9444 | 0.21723 | 0.0014681 | 919 | 135982 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
765 |  | 34840 | MANU K11 - K11 MANUREWA CENTRAL | Auckland | MANU K11 | 2024-05-29 | 45441.7965 | 2024-05-30 | 45442.6451 | 0.55318 | 0.0011342 | 710 | 346290 | Unplanned | Human error | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
766 |  | 34841 | MWEL K03 - K03 BRISCOES | Auckland | MWEL K03 | 2024-05-29 | 45441.7 | 2024-05-30 | 45442.4903 | 0.11635 | 0.00010224 | 64 | 72832 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
767 |  | 34842 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-29 | 45441.8486 | 2024-05-29 | 45441.9382 | 0.2511 | 0.0024585 | 1539 | 157184 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
768 |  | 34843 | MWEL K03 - K03 BRISCOES | Auckland | MWEL K03 | 2024-05-29 | 45441.7 | 2024-05-30 | 45442.5625 | 0.21626 | 0.00017412 | 109 | 135378 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
769 |  | 34844 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-05-29 | 45441.9042 | 2024-05-30 | 45442.2514 | 0.31287 | 0.00085465 | 535 | 195857 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
770 |  | 34845 | OTAR K17 - K17 GERALDINE AVE | Auckland | OTAR K17 | 2024-05-29 | 45441.7979 | 2024-05-30 | 45442.3576 | 0.24469 | 0.0051407 | 1673 | 153175 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
771 |  | 34846 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-29 | 45441.9451 | 2024-05-30 | 45442.3271 | 0.036901 | 6.7091e-05 | 42 | 23100 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
772 |  | 34847 | MANU K07 - K07 HALVER RD | Auckland | MANU K07 | 2024-05-29 | 45441.9458 | 2024-05-30 | 45442.1625 | 0.14105 | 0.00045208 | 283 | 88296 | Unplanned | Third party interference | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
773 |  | 34848 | MEAS K12 - K12 MASSEY RD | Auckland | MEAS K12 | 2024-05-29 | 45441.8375 | 2024-05-30 | 45442.116 | 0.26904 | 0.0017109 | 1071 | 168419 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
774 |  | 34849 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-05-29 | 45441.8375 | 2024-05-30 | 45442.6701 | 0.20268 | 0.00022365 | 140 | 126878 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
775 |  | 34852 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-30 | 45442.3493 | 2024-05-30 | 45442.634 | 0.1454 | 0.00035466 | 222 | 91020 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
776 |  | 34853 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2024-05-29 | 45441.8972 | 2024-05-30 | 45442.0056 | 0.11214 | 0.00071885 | 450 | 70200 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
777 |  | 34854 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-29 | 45441.9299 | 2024-05-30 | 45442.7014 | 0.095582 | 0.00010864 | 68 | 59834 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
778 |  | 34855 | SPUR K09 - K09 PANORAMA | Northern | SPUR K09 | 2024-05-29 | 45441.6806 | 2024-05-30 | 45442.6528 | 0.011182 | 7.987e-06 | 5 | 7000 | Unplanned | Human error | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
779 |  | 34856 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-05-29 | 45441.8604 | 2024-05-30 | 45442.1292 | 0.023492 | 6.0703e-05 | 38 | 14706 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
780 |  | 34857 | MWEL K05 - K05 MT. WELLINGTON H'WAY SOUTH | Auckland | MWEL K05 | 2024-05-29 | 45441.9194 | 2024-05-30 | 45442.4403 | 0.065895 | 8.786e-05 | 55 | 41250 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
781 |  | 34858 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-29 | 45441.7069 | 2024-05-30 | 45442.3938 | 0.022118 | 2.2364e-05 | 14 | 13846 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
782 |  | 34859 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-30 | 45442.0715 | 2024-05-31 | 45443.3465 | 0.074851 | 5.7517e-05 | 36 | 46856 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
783 |  | 34860 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2024-05-29 | 45441.9771 | 2024-05-30 | 45442.4583 | 0.026569 | 3.8339e-05 | 24 | 16632 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
784 |  | 34861 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-05-29 | 45441.9021 | 2024-05-30 | 45442.8604 | 0.015431 | 1.1182e-05 | 7 | 9660 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
785 |  | 34862 | TPAP K08 - K08 CHURCH ST WEST VIA LS | Auckland | TPAP K08 | 2024-05-30 | 45442.4826 | 2024-05-30 | 45442.7847 | 0.053507 | 0.000123 | 77 | 33495 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
786 |  | 34863 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-05-29 | 45441.7639 | 2024-05-30 | 45442.3035 | 0.6894 | 0.00089778 | 562 | 431562 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
787 |  | 34864 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-30 | 45442.5257 | 2024-05-30 | 45442.7333 | 0.050107 | 0.00040415 | 253 | 31367 | Unplanned | Third party interference | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
788 |  | 34865 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-05-30 | 45442.5271 | 2024-05-30 | 45442.5618 | 0.017971 | 0.00035943 | 225 | 11250 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
789 |  | 34867 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-30 | 45442.7118 | 2024-05-30 | 45442.7611 | 0.0049905 | 7.0288e-05 | 44 | 3124 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
790 |  | 34868 | HELE K10 - K10 KAUKAPAKAPA | Northern | HELE K10 | 2024-05-30 | 45442.3542 | 2024-05-30 | 45442.9708 | 0.0014185 | 1.597e-06 | 1 | 888 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
791 |  | 34870 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-05-30 | 45442.6444 | 2024-05-30 | 45442.8389 | 0.055017 | 0.00019649 | 123 | 34440 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
792 |  | 34872 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-30 | 45442.8431 | 2024-05-31 | 45443.0437 | 0.0237 | 0.00012778 | 61 | 14836 | Unplanned | Vegetation
793 |  | 34873 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-05-29 | 45441.8299 | 2024-05-30 | 45442.9194 | 0.29888 | 0.00030671 | 192 | 187098 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
794 |  | 34874 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-05-30 | 45442.5882 | 2024-05-30 | 45442.8785 | 0.002671 | 6.39e-06 | 4 | 1672 | Unplanned | Lightning | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
795 |  | 34875 | PAPA K13 - K13 BATES ST | Auckland | PAPA K13 | 2024-05-30 | 45442.8896 | 2024-06-01 | 45444.1042 | 0.012428 | 3.0352e-05 | 19 | 7780 | Planned | Planned
796 |  | 34876 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-30 | 45442.6076 | 2024-05-30 | 45442.8854 | 0.00063898 | 1.597e-06 | 1 | 400 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
797 |  | 34877 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-05-30 | 45442.9083 | 2024-05-31 | 45443.7736 | 0.020288 | 0.00036899 | 231 | 12700 | Unplanned | Lightning
798 |  | 34878 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-05-29 | 45441.8639 | 2024-05-31 | 45443.1215 | 0.005786 | 3.195e-06 | 2 | 3622 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
799 |  | 34879 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-05-30 | 45442.9757 | 2024-05-31 | 45443.4986 | 0.0024058 | 3.195e-06 | 2 | 1506 | Unplanned | Defective equipment
800 |  | 34880 | WAIM K05 - K05 MURIWAI | Northern | WAIM K08 | 2024-05-30 | 45442.7562 | 2024-06-01 | 45444.6521 | 0.078132 | 0.00020288 | 65 | 48910 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
801 |  | 34881 | SIMP K08 - K08 SEIBEL ROAD | Northern | SIMP K08 | 2024-05-30 | 45442.9715 | 2024-05-31 | 45443.0868 | 0.010077 | 6.0703e-05 | 38 | 6308 | Unplanned | Defective equipment
802 |  | 34882 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-05-30 | 45442.6528 | 2024-05-31 | 45443.5674 | 0.0021039 | 1.597e-06 | 1 | 1317 | Unplanned | Lightning | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
803 |  | 34883 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-05-29 | 45441.8396 | 2024-05-31 | 45443.7604 | 1.444 | 0.0016869 | 1056 | 903927 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
804 |  | 34884 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-05-30 | 45442.8833 | 2024-05-31 | 45443.1375 | 0.007016 | 1.917e-05 | 12 | 4392 | Unplanned | Cause unknown
805 |  | 34885 | RIVE K04 - K04 BARRETT RD | Northern | RIVE K04 | 2024-05-30 | 45442.7611 | 2024-05-31 | 45443.3333 | 0.013163 | 1.5974e-05 | 10 | 8240 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
806 |  | 34886 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-05-31 | 45443.3708 | 2024-05-31 | 45443.425 | 0.00099681 | 1.2779e-05 | 8 | 624 | Unplanned | Defective equipment
807 |  | 34887 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-05-31 | 45443.3681 | 2024-06-01 | 45444.5208 | 0.015093 | 2.0766e-05 | 13 | 9448 | Unplanned | Defective equipment
808 |  | 34888 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-05-31 | 45443.4507 | 2024-05-31 | 45443.6 | 0.1178 | 0.00054793 | 343 | 73745 | Unplanned | Defective equipment
809 |  | 34889 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-05-31 | 45443.275 | 2024-05-31 | 45443.3618 | 0.0075879 | 6.0704e-05 | 38 | 4750 | Unplanned | Vegetation
810 |  | 34890 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-05-31 | 45443.2354 | 2024-05-31 | 45443.4062 | 0.0027508 | 1.1182e-05 | 7 | 1722 | Unplanned | Lightning
811 |  | 34891 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-05-30 | 45442.6153 | 2024-05-31 | 45443.3986 | 0.054058 | 4.7919e-05 | 30 | 33840 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
812 |  | 34892 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-05-31 | 45443.4028 | 2024-05-31 | 45443.4167 | 9.5848e-05 | 4.792e-06 | 3 | 60 | Unplanned | Vegetation
813 |  | 34893 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-05-31 | 45443.409 | 2024-05-31 | 45443.6319 | 0.0015384 | 4.792e-06 | 3 | 963 | Unplanned | Lightning
814 |  | 34894 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-05-30 | 45442.5549 | 2024-05-31 | 45443.4479 | 0.0020543 | 1.597e-06 | 1 | 1286 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
815 |  | 34896 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-05-31 | 45443.5035 | 2024-05-31 | 45443.5451 | 0.042652 | 0.00071087 | 445 | 26700 | Unplanned | Vegetation
816 |  | 34897 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-05-30 | 45442.1764 | 2024-05-31 | 45443.6771 | 0.082851 | 3.8338e-05 | 24 | 51864 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
817 |  | 34898 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-05-31 | 45443.3472 | 2024-05-31 | 45443.9896 | 0.046492 | 0.00096487 | 484 | 29104 | Unplanned | Defective equipment
818 |  | 34899 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-05-30 | 45442.5826 | 2024-05-30 | 45442.8438 | 0.012614 | 3.3547e-05 | 21 | 7896 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
819 |  | 34900 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-31 | 45443.0271 | 2024-05-31 | 45443.5174 | 0.031579 | 4.4728e-05 | 28 | 19768 | Unplanned | Lightning
820 |  | 34901 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-05-30 | 45442.2847 | 2024-06-01 | 45444.375 | 0.0048084 | 1.597e-06 | 1 | 3010 | Unplanned | Vegetation | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
821 |  | 34902 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-05-31 | 45443.5312 | 2024-05-31 | 45443.5347 | 3.9936e-05 | 7.987e-06 | 5 | 25 | Unplanned | Cause unknown
822 |  | 34903 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-05-30 | 45442.7625 | 2024-05-31 | 45443.575 | 0.0093451 | 7.987e-06 | 5 | 5850 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
823 |  | 34904 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-05-29 | 45441.8924 | 2024-05-31 | 45443.7139 | 0.0083803 | 3.195e-06 | 2 | 5246 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
824 |  | 34905 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-05-30 | 45442.9215 | 2024-05-31 | 45443.5319 | 0.0042125 | 4.792e-06 | 3 | 2637 | Unplanned | Cause unknown
825 |  | 34906 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-05-30 | 45442.9556 | 2024-05-31 | 45443.6604 | 0.17977 | 0.00030671 | 192 | 112537 | Unplanned | Cause unknown
826 |  | 34907 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-05-31 | 45443.6208 | 2024-05-31 | 45443.691 | 0.020753 | 0.00061504 | 243 | 12991 | Unplanned | Defective equipment
827 |  | 34908 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-05-30 | 45442.616 | 2024-05-31 | 45443.6806 | 0.012245 | 7.987e-06 | 5 | 7665 | Unplanned | Lightning | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
828 |  | 34909 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-05-31 | 45443.6965 | 2024-05-31 | 45443.7312 | 0.0023962 | 4.7922e-05 | 30 | 1500 | Unplanned | Defective equipment
829 |  | 34910 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-05-30 | 45442.3187 | 2024-05-31 | 45443.5972 | 0.038232 | 2.0767e-05 | 13 | 23933 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
830 |  | 34911 | BRIC K05 - K05 PORTAGE RD | Northern | BRIC K05 | 2024-05-31 | 45443.6618 | 2024-05-31 | 45443.684 | 5.1119e-05 | 1.597e-06 | 1 | 32 | Unplanned | Defective equipment
831 |  | 34912 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-05-31 | 45443.4361 | 2024-05-31 | 45443.6889 | 0.00058148 | 1.597e-06 | 1 | 364 | Unplanned | Cause unknown
832 |  | 34913 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-05-31 | 45443.3604 | 2024-05-31 | 45443.7361 | 0.010371 | 1.917e-05 | 12 | 6492 | Unplanned | Cause unknown
833 |  | 34914 | WAIR K12 - K12 ARCHERS ROAD | Northern | WAIR K12 | 2024-05-31 | 45443.4729 | 2024-05-31 | 45443.6076 | 0.022623 | 0.00011661 | 73 | 14162 | Unplanned | Cause unknown
834 |  | 34915 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-05-31 | 45443.5271 | 2024-05-31 | 45443.6146 | 0.00020128 | 1.597e-06 | 1 | 126 | Unplanned | Cause unknown
835 |  | 34916 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-05-31 | 45443.4715 | 2024-05-31 | 45443.8868 | 0.021016 | 3.5144e-05 | 22 | 13156 | Unplanned | Defective equipment
836 |  | 34917 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-05-29 | 45441.7861 | 2024-06-01 | 45444.125 | 0.01108 | 1.5976e-05 | 10 | 6936 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
837 |  | 34918 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-05-31 | 45443.2451 | 2024-06-01 | 45444.0215 | 0.0053579 | 4.792e-06 | 3 | 3354 | Unplanned | Lightning
838 |  | 34919 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-05-31 | 45443.0764 | 2024-06-01 | 45444.0521 | 0.015711 | 1.1182e-05 | 7 | 9835 | Unplanned | Cause unknown
839 |  | 34920 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-05-31 | 45443.6722 | 2024-06-01 | 45444.2083 | 0.0036997 | 4.791e-06 | 3 | 2316 | Unplanned | Cause unknown
840 |  | 34921 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-05-31 | 45443.6896 | 2024-06-01 | 45444.6917 | 0.0092205 | 6.39e-06 | 4 | 5772 | Unplanned | Vegetation
841 |  | 34922 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-05-31 | 45443.384 | 2024-06-02 | 45445.5625 | 0.0050112 | 1.597e-06 | 1 | 3137 | Unplanned | Defective equipment
842 |  | 34923 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-05-31 | 45443.6014 | 2024-06-01 | 45444.4437 | 0.0019377 | 1.597e-06 | 1 | 1213 | Unplanned | Cause unknown
843 |  | 34925 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K09 | 2024-05-31 | 45443.6028 | 2024-06-01 | 45444.5896 | 0.00227 | 1.597e-06 | 1 | 1421 | Unplanned | Lightning
844 |  | 34926 | MKIN K04 - K04 COLISEUM DRIVE | Northern | MKIN K04 | 2024-06-01 | 45444.3764 | 2024-06-01 | 45444.6708 | 0.014901 | 3.5144e-05 | 22 | 9328 | Planned | Planned
845 |  | 34927 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-06-01 | 45444.5326 | 2024-06-01 | 45444.6847 | 0.00069969 | 3.195e-06 | 2 | 438 | Unplanned | Lightning
846 |  | 34928 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-01 | 45444.6521 | 2024-06-02 | 45445.6854 | 0.002377 | 1.597e-06 | 1 | 1488 | Unplanned | Vegetation
847 |  | 34929 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-06-01 | 45444.8264 | 2024-06-01 | 45444.9083 | 0.001131 | 9.585e-06 | 6 | 708 | Unplanned | Defective equipment
848 |  | 34931 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-06-01 | 45444.3764 | 2024-06-02 | 45445.3701 | 0.0045719 | 3.195e-06 | 2 | 2862 | Unplanned | Cause unknown
849 |  | 34932 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-05-29 | 45441.6368 | 2024-06-02 | 45445.4424 | 0.0087541 | 1.597e-06 | 1 | 5480 | Unplanned | Defective equipment | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
850 |  | 34933 | WAIK K05 - K05 WEST COAST ROAD | Northern | WAIK K05 | 2024-06-02 | 45445.4972 | 2024-06-02 | 45445.5153 | 0.033476 | 0.0012875 | 806 | 20956 | Unplanned | Third party interference
851 |  | 34934 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-05-31 | 45443.5375 | 2024-06-02 | 45445.625 | 0.0096039 | 3.195e-06 | 2 | 6012 | Unplanned | Defective equipment
852 |  | 34935 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-06-03 | 45446.0451 | 2024-06-03 | 45446.0764 | 0.028642 | 0.00077319 | 484 | 17930 | Unplanned | Cause unknown
853 |  | 34936 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-06-03 | 45446.9583 | 2024-06-04 | 45447.0222 | 0.016931 | 0.00021087 | 132 | 10599 | Planned | Planned
854 |  | 34937 | BMON K03 - K03 CENTRAL | Northern | BMON K03 | 2024-06-04 | 45447.8333 | 2024-06-04 | 45447.9243 | 0.053991 | 0.00041214 | 258 | 33798 | Planned | Planned
855 |  | 34938 | HBUR K11 - K11 HAMMOND PL | Northern | HBUR K11 | 2024-06-05 | 45448.3333 | 2024-06-05 | 45448.6931 | 0.2168 | 0.00041853 | 262 | 135716 | Planned | Planned
856 |  | 34939 | BRIC K04 - K04 LINKS RD | Northern | BRIC K04 | 2024-06-05 | 45448.3333 | 2024-06-05 | 45448.6757 | 0.032289 | 6.5496e-05 | 41 | 20213 | Planned | Planned
857 |  | 34940 | SHOW K09 - K09 KURNELL DR | Auckland | SHOW K09 | 2024-06-05 | 45448.375 | 2024-06-05 | 45448.5486 | 0.032748 | 0.00013099 | 82 | 20500 | Planned | Planned
858 |  | 34941 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-06-05 | 45448.3562 | 2024-06-05 | 45448.7083 | 0.037256 | 7.3477e-05 | 46 | 23322 | Planned | Planned
859 |  | 34942 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-05 | 45448.3917 | 2024-06-05 | 45448.3938 | 4.792e-06 | 1.597e-06 | 1 | 3 | Planned | Planned
860 |  | 34943 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-06-05 | 45448.4243 | 2024-06-05 | 45448.5556 | 0.00030192 | 1.597e-06 | 1 | 189 | Unplanned | Defective equipment
861 |  | 34944 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-05 | 45448.441 | 2024-06-05 | 45448.4556 | 0.00013419 | 6.39e-06 | 4 | 84 | Planned | Planned
862 |  | 34945 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-05 | 45448.5208 | 2024-06-05 | 45448.5278 | 1.5975e-05 | 1.597e-06 | 1 | 10 | Planned | Planned
863 |  | 34946 | 11kV BUS - SUNS 11kV BUSBAR | Northern | SUNS K10 | 2024-06-05 | 45448.5472 | 2024-06-05 | 45448.634 | 0.0011981 | 9.586e-06 | 6 | 750 | Planned | Planned
864 |  | 34947 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-06-05 | 45448.4819 | 2024-06-05 | 45448.6493 | 0.0090879 | 4.6325e-05 | 29 | 5689 | Unplanned | Third party interference
865 |  | 34948 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-05 | 45448.5861 | 2024-06-05 | 45448.5944 | 0.00017253 | 1.4377e-05 | 9 | 108 | Planned | Planned
866 |  | 34950 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-05 | 45448.6493 | 2024-06-05 | 45448.6597 | 7.1886e-05 | 4.792e-06 | 3 | 45 | Planned | Planned
867 |  | 34951 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-06-05 | 45448.8194 | 2024-06-05 | 45448.8264 | 0.00011182 | 1.1182e-05 | 7 | 70 | Unplanned | Cause unknown
868 |  | 34952 | HANS K27 - K27 NIKAU ROAD | Auckland | HANS K27 | 2024-06-05 | 45448.9799 | 2024-06-06 | 45449.1882 | 0.047726 | 0.0003163 | 198 | 29876 | Planned | Planned
869 |  | 34953 | HOBS K36 - K36 PRICE WATERHOUSE | Auckland | HOBS K36 | 2024-06-05 | 45448.9792 | 2024-06-06 | 45449.125 | 0.0070448 | 3.3547e-05 | 21 | 4410 | Planned | Planned
870 |  | 34954 | TRIA K05 - K05 NORTH | Northern | TRIA K05 | 2024-06-06 | 45449.3 | 2024-06-06 | 45449.7354 | 0.0087876 | 2.0767e-05 | 12 | 5501 | Planned | Planned
871 |  | 34955 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-06 | 45449.3549 | 2024-06-06 | 45449.7722 | 0.097055 | 0.00067415 | 262 | 60756 | Planned | Planned
872 |  | 34956 | NLYN K01 - K01 ARAWA ST | Northern | NLYN K01 | 2024-06-06 | 45449.3771 | 2024-06-06 | 45449.6549 | 0.15847 | 0.00039617 | 248 | 99200 | Planned | Planned
873 |  | 34957 | FBSH K07 - K07 PENCAITLAND DR SOUTH | Auckland | FBSH K07 | 2024-06-06 | 45449.3757 | 2024-06-06 | 45449.6062 | 0.028109 | 8.4665e-05 | 53 | 17596 | Planned | Planned
874 |  | 34958 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-06-06 | 45449.375 | 2024-06-06 | 45449.5708 | 0.00090097 | 3.195e-06 | 2 | 564 | Planned | Planned
875 |  | 34960 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-06-06 | 45449.4194 | 2024-06-06 | 45449.6583 | 0.0010991 | 3.195e-06 | 2 | 688 | Planned | Planned
876 |  | 34961 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-06-06 | 45449.4201 | 2024-06-06 | 45449.5347 | 0.0042173 | 2.5559e-05 | 16 | 2640 | Planned | Planned
877 |  | 34962 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-06-06 | 45449.441 | 2024-06-06 | 45449.625 | 0.0084665 | 3.1948e-05 | 20 | 5300 | Unplanned | Defective equipment
878 |  | 34963 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-06-06 | 45449.6236 | 2024-06-06 | 45449.6875 | 0.00029393 | 3.195e-06 | 2 | 184 | Unplanned | Third party interference
879 |  | 34964 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-06 | 45449.7722 | 2024-06-06 | 45449.8708 | 0.20471 | 0.0022092 | 1223 | 128146 | Unplanned | Defective equipment
880 |  | 34964 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K09 | 2024-06-06 | 45449.7722 | 2024-06-06 | 45449.8708 | 0.038288 | 0.0010255 | 642 | 23968 | Unplanned | Defective equipment
881 |  | 34965 | PAKU K10 - K10 GRAMMAR SCHOOL RD | Auckland | PAKU K10 | 2024-06-06 | 45449.9174 | 2024-06-15 | 45458.1271 | 0.053911 | 0.00016614 | 52 | 33748 | Planned | Planned
882 |  | 34966 | FREE K13 - K13 WILKINS ST (5) | Auckland | FREE K56 | 2024-06-06 | 45449.9167 | 2024-06-07 | 45450.0139 | 0.00022364 | 1.597e-06 | 1 | 140 | Planned | Planned
883 |  | 34967 | WIRI K02 - K02 KENDERDINE RD | Auckland | WIRI K02 | 2024-06-07 | 45450.3174 | 2024-06-07 | 45450.4785 | 0.09915 | 0.00049521 | 310 | 62067 | Unplanned | Wildlife
884 |  | 34969 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-07 | 45450.3569 | 2024-06-07 | 45450.6528 | 0.06601 | 0.00015495 | 97 | 41322 | Planned | Planned
885 |  | 34970 | TORB K07 - K07 GLAMORGAN DRIVE | Northern | TORB K07 | 2024-06-07 | 45450.3549 | 2024-06-07 | 45450.7056 | 0.18474 | 0.00036582 | 229 | 115645 | Planned | Planned
886 |  | 34971 | SUNS K10 - K10 MATTHEWS ROAD + LS | Northern | SUNS K10 | 2024-06-07 | 45450.375 | 2024-06-07 | 45450.4632 | 0.0012173 | 9.583e-06 | 6 | 762 | Planned | Planned
887 |  | 34972 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-06-07 | 45450.375 | 2024-06-07 | 45450.684 | 0.020615 | 4.6325e-05 | 29 | 12905 | Planned | Planned
888 |  | 34973 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-06-07 | 45450.3521 | 2024-06-07 | 45450.7875 | 0.12188 | 0.0011087 | 386 | 76298 | Planned | Planned
889 |  | 34974 | ONEH K09 - K09 - GREY ST | Auckland | ONEH K09 | 2024-06-07 | 45450.4056 | 2024-06-07 | 45450.5875 | 0.042272 | 0.00016134 | 101 | 26462 | Planned | Planned
890 |  | 34975 | RBEA K06 - K06 VIPOND RD | Northern | RBEA K06 | 2024-06-07 | 45450.375 | 2024-06-07 | 45450.5597 | 0.016997 | 6.3898e-05 | 40 | 10640 | Planned | Planned
891 |  | 34976 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-07 | 45450.3819 | 2024-06-07 | 45450.4521 | 0.0041949 | 4.1532e-05 | 26 | 2626 | Planned | Planned
892 |  | 34977 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-06-07 | 45450.5632 | 2024-06-07 | 45450.6111 | 0.00022045 | 3.194e-06 | 2 | 138 | Unplanned | Cause unknown
893 |  | 34978 | MEAS K13 - K13 BUCKLAND RD | Auckland | MEAS K13 | 2024-06-07 | 45450.7701 | 2024-06-07 | 45450.9028 | 0.13168 | 0.0023499 | 1471 | 82428 | Unplanned | Defective equipment
894 |  | 34979 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-06-07 | 45450.9313 | 2024-06-08 | 45451.2181 | 0.12601 | 0.00030512 | 191 | 78883 | Planned | Planned
895 |  | 34980 | HILL K02 - K02 72 HILLSBOROUGH RD | Auckland | HILL K02 | 2024-06-08 | 45451.0153 | 2024-06-08 | 45451.1667 | 0.037876 | 0.00018051 | 113 | 23710 | Planned | Planned
896 |  | 34981 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-06-08 | 45451.0861 | 2024-06-08 | 45451.1764 | 0.0037381 | 2.8754e-05 | 18 | 2340 | Planned | Planned
897 |  | 34982 | SABU K01 - K01 ST LEONARDS RD + LS | Northern | SABU K01 | 2024-06-08 | 45451.3479 | 2024-06-08 | 45451.7486 | 0.1189 | 0.00020607 | 129 | 74433 | Planned | Planned
898 |  | 34983 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2024-06-08 | 45451.3764 | 2024-06-08 | 45451.6681 | 0.048978 | 0.00011661 | 73 | 30660 | Planned | Planned
899 |  | 34984 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-08 | 45451.2014 | 2024-06-08 | 45451.3347 | 0.0033738 | 1.7572e-05 | 11 | 2112 | Unplanned | Cause unknown
900 |  | 34985 | MCEN K01 - K01 MANGERE BRIDGE | Auckland | MCEN K01 | 2024-06-08 | 45451.5889 | 2024-06-08 | 45451.6465 | 0.10686 | 0.003179 | 1990 | 66894 | Unplanned | Third party interference
901 |  | 34986 | PAPA K13 - K13 BATES ST | Auckland | PAPA K13 | 2024-06-08 | 45451.8812 | 2024-06-09 | 45452.191 | 0.013537 | 3.0352e-05 | 19 | 8474 | Planned | Planned
902 |  | 34987 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-06-09 | 45452.375 | 2024-06-09 | 45452.6458 | 0.0087221 | 2.2364e-05 | 14 | 5460 | Planned | Planned
903 |  | 34988 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-06-09 | 45452.3313 | 2024-06-09 | 45452.4097 | 0.00072205 | 6.39e-06 | 4 | 452 | Unplanned | Vegetation
904 |  | 34990 | TORB K11 - K11 BEACH ROAD | Northern | TORB K11 | 2024-06-09 | 45452.6146 | 2024-06-09 | 45452.6674 | 0.13097 | 0.0027988 | 1752 | 81987 | Unplanned | Defective equipment
905 |  | 34993 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-06-09 | 45452.6083 | 2024-06-09 | 45452.7083 | 0.0027604 | 1.917e-05 | 12 | 1728 | Unplanned | Cause unknown
906 |  | 34994 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-06-09 | 45452.6799 | 2024-06-09 | 45452.8097 | 0.06963 | 0.00076039 | 476 | 43588 | Unplanned | Vegetation
907 |  | 34995 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-06-09 | 45452.5861 | 2024-06-09 | 45452.691 | 0.0016885 | 1.1182e-05 | 7 | 1057 | Unplanned | Vegetation
908 |  | 34997 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-09 | 45452.8097 | 2024-06-09 | 45452.8257 | 0.0057157 | 0.0002556 | 160 | 3578 | Unplanned | Cause unknown
909 |  | 34998 | LAIN K08 - K08 HUIA PUMPS | Northern | LAIN K08 | 2024-06-09 | 45452.8222 | 2024-06-09 | 45452.8778 | 0.00063899 | 7.987e-06 | 5 | 400 | Unplanned | Third party interference
910 |  | 35000 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-06-09 | 45452.9229 | 2024-06-10 | 45453.1215 | 0.0091375 | 3.1949e-05 | 20 | 5720 | Unplanned | Vegetation
911 |  | 35002 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-10 | 45453.3556 | 2024-06-10 | 45453.7021 | 0.037465 | 7.5078e-05 | 47 | 23453 | Planned | Planned
912 |  | 35003 | RBEA K05 - K05 JELAS RD | Northern | RBEA K05 | 2024-06-10 | 45453.3604 | 2024-06-10 | 45453.709 | 0.070144 | 0.00014057 | 88 | 43910 | Planned | Planned
913 |  | 35004 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-06-10 | 45453.4389 | 2024-06-10 | 45453.7243 | 0.12015 | 0.00029234 | 183 | 75213 | Planned | Planned
914 |  | 35005 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-06-10 | 45453.5264 | 2024-06-10 | 45453.5312 | 3.3547e-05 | 4.792e-06 | 3 | 21 | Unplanned | Other Cause | Outage caused by Tap Operation
915 |  | 35006 | NGAT K02 - K02 STANLEY POINT | Northern | NGAT K02 | 2024-06-10 | 45453.85 | 2024-06-12 | 45455.0896 | 0.015542 | 0.00015016 | 47 | 9729 | Unplanned | Defective equipment
916 |  | 35007 | HVAL K02 - K02 CORBAN AVENUE | Northern | HVAL K02 | 2024-06-10 | 45453.8639 | 2024-06-10 | 45453.916 | 0.003115 | 4.1534e-05 | 26 | 1950 | Unplanned | Defective equipment
917 |  | 35008 | FREE K13 - K13 WILKINS ST (5) | Auckland | FREE K56 | 2024-06-10 | 45453.9167 | 2024-06-10 | 45453.9799 | 0.00014537 | 1.597e-06 | 1 | 91 | Planned | Planned
918 |  | 35010 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-06-11 | 45454.3333 | 2024-06-11 | 45454.6687 | 0.060954 | 0.00012619 | 79 | 38157 | Planned | Planned
919 |  | 35011 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-06-11 | 45454.3549 | 2024-06-11 | 45454.7264 | 0.014529 | 2.7157e-05 | 17 | 9095 | Planned | Planned
920 |  | 35012 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-06-11 | 45454.3569 | 2024-06-11 | 45454.7153 | 0.19371 | 0.0003754 | 235 | 121260 | Planned | Planned
921 |  | 35014 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-11 | 45454.7153 | 2024-06-11 | 45454.9375 | 0.081627 | 0.0002556 | 160 | 51098 | Unplanned | Defective equipment
922 |  | 35015 | FREE K12 - K12 WESTHAVEN DR (31) | Auckland | FREE K51 | 2024-06-11 | 45454.9375 | 2024-06-12 | 45455.1458 | 0.0038339 | 1.2779e-05 | 8 | 2400 | Planned | Planned
923 |  | 35017 | CHEV K03 - K03 ACC WESTERN GARDENS | Auckland | CHEV K03 | 2024-06-12 | 45455.2083 | 2024-06-12 | 45455.2431 | 0.01278 | 0.00025559 | 160 | 8000 | Planned | Planned
924 |  | 35018 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2024-06-12 | 45455.2132 | 2024-06-12 | 45455.7542 | 0.17804 | 0.0027444 | 1587 | 111455 | Unplanned | Third party interference
925 |  | 35019 | ORAT K02 - K02 PARKER ROAD | Northern | ORAT K02 | 2024-06-12 | 45455.334 | 2024-06-12 | 45455.6285 | 0.041643 | 0.00012141 | 76 | 26068 | Planned | Planned
926 |  | 35020 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-06-12 | 45455.3549 | 2024-06-12 | 45455.6236 | 0.0043275 | 1.1182e-05 | 7 | 2709 | Planned | Planned
927 |  | 35021 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-06-12 | 45455.3576 | 2024-06-12 | 45455.6458 | 0.023521 | 5.7512e-05 | 36 | 14724 | Planned | Planned
928 |  | 35022 | BLMN K01 - K01 ISLAND BAY | Northern | BLMN K01 | 2024-06-12 | 45455.3785 | 2024-06-12 | 45455.6868 | 0.19008 | 0.00042812 | 268 | 118992 | Planned | Planned
929 |  | 35023 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-12 | 45455.25 | 2024-06-12 | 45455.5243 | 0.0017093 | 1.5976e-05 | 5 | 1070 | Unplanned | Wildlife
930 |  | 35024 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-06-12 | 45455.3965 | 2024-06-12 | 45455.6944 | 0.021245 | 4.9519e-05 | 31 | 13299 | Planned | Planned
931 |  | 35025 | TAKA K12 - K12 MILL RD | Auckland | MKAU K19 | 2024-06-12 | 45455.3528 | 2024-06-12 | 45455.4375 | 0.00019489 | 1.597e-06 | 1 | 122 | Unplanned | Wildlife
932 |  | 35027 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-06-12 | 45455.7188 | 2024-06-13 | 45456.075 | 0.049846 | 0.0001262 | 79 | 31203 | Unplanned | Third party interference
933 |  | 35028 | SABU K01 - K01 ST LEONARDS RD + LS | Northern | SABU K01 | 2024-06-12 | 45455.4764 | 2024-06-12 | 45455.9618 | 0.059181 | 8.4665e-05 | 53 | 37047 | Unplanned | Defective equipment
934 |  | 35029 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-06-12 | 45455.8514 | 2024-06-13 | 45456.1306 | 0.0064218 | 1.5974e-05 | 10 | 4020 | Planned | Planned
935 |  | 35031 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-06-12 | 45455.9757 | 2024-06-13 | 45456.184 | 0.10233 | 0.00083223 | 521 | 64059 | Unplanned | Cause unknown
936 |  | 35032 | JAME K08 - K08 GLENFIELD ROAD | Northern | JAME K08 | 2024-06-13 | 45456.3438 | 2024-06-13 | 45456.6458 | 0.03405 | 7.8276e-05 | 49 | 21315 | Planned | Planned
937 |  | 35033 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-06-13 | 45456.3556 | 2024-06-13 | 45456.6181 | 0.063753 | 0.00056232 | 243 | 39909 | Planned | Planned
938 |  | 35034 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-06-13 | 45456.3757 | 2024-06-13 | 45456.6778 | 0.26198 | 0.00060224 | 377 | 163995 | Planned | Planned
939 |  | 35035 | RIVE K08 - K08 ACCESS RD | Northern | RIVE K08 | 2024-06-13 | 45456.3542 | 2024-06-13 | 45456.5819 | 0.00052397 | 1.597e-06 | 1 | 328 | Planned | Planned
940 |  | 35036 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-06-13 | 45456.4062 | 2024-06-13 | 45456.6181 | 0.0034106 | 1.1182e-05 | 7 | 2135 | Planned | Planned
941 |  | 35037 | KKAP K06 - K06 PEAK RD | Northern | KKAP K06 | 2024-06-13 | 45456.4611 | 2024-06-13 | 45456.5368 | 0.037074 | 0.00042014 | 263 | 23208 | Unplanned | Cause unknown
942 |  | 35038 | BAIR K02 - K02 KERWYN AVE | Auckland | BAIR K02 | 2024-06-13 | 45456.5917 | 2024-06-14 | 45457.0569 | 0.0010623 | 3.196e-06 | 1 | 665 | Unplanned | Defective equipment
943 |  | 35039 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-06-13 | 45456.7486 | 2024-06-13 | 45456.7667 | 0.0029074 | 0.00011182 | 70 | 1820 | Unplanned | Cause unknown
944 |  | 35040 | MANL K05 - K05 ARKLES BAY | Northern | MANL K05 | 2024-06-13 | 45456.8181 | 2024-06-13 | 45456.8979 | 0.0062461 | 5.4314e-05 | 34 | 3910 | Unplanned | Defective equipment
945 |  | 35042 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-06-14 | 45457.1243 | 2024-06-14 | 45457.5521 | 0.30566 | 0.00049684 | 311 | 191340 | Unplanned | Vegetation
946 |  | 35043 | HANS K27 - K27 NIKAU ROAD | Auckland | HANS K27 | 2024-06-13 | 45456.9799 | 2024-06-14 | 45457.2132 | 0.040793 | 0.00012141 | 76 | 25536 | Planned | Planned
947 |  | 35044 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-06-14 | 45457.3542 | 2024-06-14 | 45457.6785 | 0.0029841 | 6.389e-06 | 4 | 1868 | Planned | Planned
948 |  | 35047 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-14 | 45457.4896 | 2024-06-14 | 45457.5 | 9.5848e-05 | 6.39e-06 | 4 | 60 | Unplanned | Other Cause | Outage caused by Tap Operation
949 |  | 35048 | MARA K10 - K10 OMANA BEACH RD | Auckland | MARA K10 | 2024-06-14 | 45457.4958 | 2024-06-14 | 45457.541 | 0.022091 | 0.00034665 | 217 | 13829 | Unplanned | Cause unknown
950 |  | 35049 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-14 | 45457.5424 | 2024-06-14 | 45457.8993 | 0.1675 | 0.00032588 | 204 | 104856 | Unplanned | Cause unknown
951 |  | 35050 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-06-14 | 45457.5437 | 2024-06-14 | 45457.6868 | 0.00032269 | 4.791e-06 | 1 | 202 | Unplanned | Other Cause | Outage on Non-Vector asset
952 |  | 35060 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-06-14 | 45457.8806 | 2024-06-15 | 45458.1118 | 0.0516 | 0.00015495 | 97 | 32301 | Unplanned | Vegetation
953 |  | 35061 | MWEL K05 - K05 MT. WELLINGTON H'WAY SOUTH | Auckland | MWEL K05 | 2024-06-14 | 45457.9187 | 2024-06-15 | 45458.2243 | 0.12441 | 0.00028275 | 177 | 77880 | Planned | Planned
954 |  | 35062 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-06-14 | 45457.791 | 2024-06-14 | 45457.941 | 0.0055208 | 2.5557e-05 | 16 | 3456 | Unplanned | Cause unknown
955 |  | 35063 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-06-14 | 45457.9083 | 2024-06-14 | 45457.9549 | 0.0014984 | 2.2364e-05 | 14 | 938 | Unplanned | Cause unknown
956 |  | 35064 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-15 | 45458.1701 | 2024-06-15 | 45458.4569 | 0.0074378 | 1.9171e-05 | 12 | 4656 | Unplanned | Vegetation
957 |  | 35065 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-15 | 45458.3542 | 2024-06-15 | 45458.6458 | 0.044953 | 0.00010703 | 67 | 28140 | Planned | Planned
958 |  | 35066 | TRIA K03 - K03 COLWILL RD | Northern | TRIA K03 | 2024-06-15 | 45458.3785 | 2024-06-15 | 45458.7792 | 0.093129 | 0.00016454 | 103 | 58298 | Planned | Planned
959 |  | 35066 | TRIA K03 - K03 COLWILL RD | Northern | TRIA K09 | 2024-06-15 | 45458.3785 | 2024-06-15 | 45458.7792 | 0.2627 | 0.00045688 | 286 | 164450 | Planned | Planned
960 |  | 35067 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-06-15 | 45458.375 | 2024-06-15 | 45458.6535 | 0.050606 | 0.0001262 | 79 | 31679 | Planned | Planned
961 |  | 35068 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2024-06-15 | 45458.3556 | 2024-06-15 | 45458.7486 | 0.029837 | 5.2716e-05 | 33 | 18678 | Planned | Planned
962 |  | 35069 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-06-15 | 45458.3049 | 2024-06-15 | 45458.4708 | 0.00076359 | 3.195e-06 | 2 | 478 | Unplanned | Cause unknown
963 |  | 35070 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-06-14 | 45457.8708 | 2024-06-15 | 45458.659 | 0.0036262 | 3.195e-06 | 2 | 2270 | Unplanned | Cause unknown
964 |  | 35071 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-06-15 | 45458.8021 | 2024-06-17 | 45460.6778 | 1.1679 | 0.00049683 | 311 | 731071 | Unplanned | Vegetation
965 |  | 35073 | PARN K03 - K03 FARNHAM ST | Auckland | PARN K03 | 2024-06-16 | 45459.0028 | 2024-06-16 | 45459.0875 | 0.00019489 | 1.597e-06 | 1 | 122 | Planned | Planned
966 |  | 35074 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-16 | 45459.0729 | 2024-06-16 | 45459.7319 | 0.11208 | 0.0027699 | 1721 | 70160 | Unplanned | Third party interference
967 |  | 35075 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-06-16 | 45459.2792 | 2024-06-16 | 45459.4021 | 0.02886 | 0.00065815 | 412 | 18066 | Unplanned | Vegetation
968 |  | 35076 | TAKA K13 - K13 COSGROVE RD | Auckland | TAKA K13 | 2024-06-16 | 45459.6382 | 2024-06-16 | 45459.9958 | 0.74846 | 0.0026214 | 1641 | 468534 | Unplanned | Third party interference
969 |  | 35077 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-06-16 | 45459.8347 | 2024-06-17 | 45460.2611 | 0.030406 | 4.9521e-05 | 31 | 19034 | Planned | Planned
970 |  | 35079 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-06-16 | 45459.975 | 2024-06-17 | 45460.4278 | 0.32995 | 0.0020032 | 1254 | 206548 | Unplanned | Third party interference
971 |  | 35080 | BAIR K03 - K03 BAIRDS ROAD WEST VIA LS | Auckland | BAIR K03 | 2024-06-17 | 45460.0833 | 2024-06-17 | 45460.1701 | 0.0045927 | 3.6741e-05 | 23 | 2875 | Planned | Planned
972 |  | 35081 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-17 | 45460.0833 | 2024-06-17 | 45460.2014 | 0.024948 | 0.00016294 | 102 | 15617 | Planned | Planned
973 |  | 35082 | BAIR K03 - K03 BAIRDS ROAD WEST VIA LS | Auckland | BAIR K03 | 2024-06-17 | 45460.1701 | 2024-06-17 | 45460.559 | 0.020601 | 3.8339e-05 | 24 | 12896 | Unplanned | Defective equipment
974 |  | 35083 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-17 | 45460.1465 | 2024-06-17 | 45460.2042 | 0.0025192 | 3.0351e-05 | 19 | 1577 | Unplanned | Wildlife
975 |  | 35085 | WAIM - Waimauku | Northern | BROW K02 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.029879 | 0.0018674 | 1169 | 18704 | Unplanned | Lightning
976 |  | 35085 | WAIM - Waimauku | Northern | BROW K03 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.014492 | 0.00090575 | 567 | 9072 | Unplanned | Lightning
977 |  | 35085 | WAIM - Waimauku | Northern | BROW K04 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.031336 | 0.0019585 | 1226 | 19616 | Unplanned | Lightning
978 |  | 35085 | WAIM - Waimauku | Northern | BROW K05 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.018786 | 0.0011741 | 735 | 11760 | Unplanned | Lightning
979 |  | 35085 | WAIM - Waimauku | Northern | BROW K09 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.025446 | 0.0029937 | 937 | 15929 | Unplanned | Lightning
980 |  | 35085 | WAIM - Waimauku | Northern | BROW K10 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.012954 | 0.001524 | 477 | 8109 | Unplanned | Lightning
981 |  | 35085 | WAIM - Waimauku | Northern | BROW K11 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.030633 | 0.0036039 | 1128 | 19176 | Unplanned | Lightning
982 |  | 35085 | WAIM - Waimauku | Northern | BROW K12 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.013225 | 0.0015559 | 487 | 8279 | Unplanned | Lightning
983 |  | 35085 | WAIM - Waimauku | Northern | ECOA K01 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.027783 | 0.0017364 | 1087 | 17392 | Unplanned | Lightning
984 |  | 35085 | WAIM - Waimauku | Northern | ECOA K02 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.017559 | 0.0010975 | 687 | 10992 | Unplanned | Lightning
985 |  | 35085 | WAIM - Waimauku | Northern | ECOA K04 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.03269 | 0.0020432 | 1279 | 20464 | Unplanned | Lightning
986 |  | 35085 | WAIM - Waimauku | Northern | ECOA K05 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.012703 | 0.00079393 | 497 | 7952 | Unplanned | Lightning
987 |  | 35085 | WAIM - Waimauku | Northern | ECOA K07 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.024997 | 0.0015623 | 978 | 15648 | Unplanned | Lightning
988 |  | 35085 | WAIM - Waimauku | Northern | ECOA K08 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.019323 | 0.0012077 | 756 | 12096 | Unplanned | Lightning
989 |  | 35085 | WAIM - Waimauku | Northern | ECOA K09 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 2.5559e-05 | 1.595e-06 | 1 | 16 | Unplanned | Lightning
990 |  | 35085 | WAIM - Waimauku | Northern | MKIN K01 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0093931 | 0.0013419 | 840 | 5880 | Unplanned | Lightning
991 |  | 35085 | WAIM - Waimauku | Northern | MKIN K02 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.00084985 | 0.00012141 | 76 | 532 | Unplanned | Lightning
992 |  | 35085 | WAIM - Waimauku | Northern | MKIN K03 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0 | 0 | 0 | 0 | Unplanned | Lightning
993 |  | 35085 | WAIM - Waimauku | Northern | MKIN K04 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0095943 | 0.0013706 | 858 | 6006 | Unplanned | Lightning
994 |  | 35085 | WAIM - Waimauku | Northern | MKIN K07 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0026358 | 0.0004393 | 275 | 1650 | Unplanned | Lightning
995 |  | 35085 | WAIM - Waimauku | Northern | MKIN K08 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0025591 | 0.00042652 | 267 | 1602 | Unplanned | Lightning
996 |  | 35085 | WAIM - Waimauku | Northern | MKIN K10 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0090001 | 0.0015 | 939 | 5634 | Unplanned | Lightning
997 |  | 35085 | WAIM - Waimauku | Northern | MKIN K11 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.014042 | 0.0023403 | 1465 | 8790 | Unplanned | Lightning
998 |  | 35085 | WAIM - Waimauku | Northern | MKIN K12 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 3.834e-05 | 6.388e-06 | 4 | 24 | Unplanned | Lightning
999 |  | 35085 | WAIM - Waimauku | Northern | RDAL K02 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0003131 | 2.2364e-05 | 14 | 196 | Unplanned | Lightning
1000 |  | 35085 | WAIM - Waimauku | Northern | RDAL K03 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.00039617 | 1.596e-06 | 1 | 248 | Unplanned | Lightning
1001 |  | 35085 | WAIM - Waimauku | Northern | RDAL K05 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0082301 | 0.00058786 | 368 | 5152 | Unplanned | Lightning
1002 |  | 35085 | WAIM - Waimauku | Northern | RDAL K08 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0094602 | 0.00067574 | 423 | 5922 | Unplanned | Lightning
1003 |  | 35085 | WAIM - Waimauku | Northern | RDAL K09 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0057253 | 0.00040895 | 256 | 3584 | Unplanned | Lightning
1004 |  | 35085 | WAIM - Waimauku | Northern | RDAL K11 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.015253 | 0.0010895 | 682 | 9548 | Unplanned | Lightning
1005 |  | 35085 | WAIM - Waimauku | Northern | RDAL K12 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0085879 | 0.00061343 | 384 | 5376 | Unplanned | Lightning
1006 |  | 35085 | WAIM - Waimauku | Northern | TORB K07 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.037007 | 0.0014233 | 891 | 23166 | Unplanned | Lightning
1007 |  | 35085 | WAIM - Waimauku | Northern | TORB K08 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.031649 | 0.0012173 | 762 | 19812 | Unplanned | Lightning
1008 |  | 35085 | WAIM - Waimauku | Northern | TORB K10 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.020019 | 0.00076998 | 482 | 12532 | Unplanned | Lightning
1009 |  | 35085 | WAIM - Waimauku | Northern | TORB K11 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.073307 | 0.0028195 | 1765 | 45890 | Unplanned | Lightning
1010 |  | 35085 | WAIM - Waimauku | Northern | WAIA K01 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.035368 | 0.0026199 | 820 | 22140 | Unplanned | Lightning
1011 |  | 35085 | WAIM - Waimauku | Northern | WAIA K02 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.040198 | 0.0029777 | 932 | 25164 | Unplanned | Lightning
1012 |  | 35085 | WAIM - Waimauku | Northern | WAIA K04 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.050593 | 0.0037477 | 1173 | 31671 | Unplanned | Lightning
1013 |  | 35085 | WAIM - Waimauku | Northern | WAIA K05 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.011818 | 0.00087542 | 274 | 7398 | Unplanned | Lightning
1014 |  | 35085 | WAIM - Waimauku | Northern | WAIM K02 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0075528 | 0.00062942 | 394 | 4728 | Unplanned | Lightning
1015 |  | 35085 | WAIM - Waimauku | Northern | WAIM K03 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.0055703 | 0.00050636 | 317 | 3487 | Unplanned | Lightning
1016 |  | 35085 | WAIM - Waimauku | Northern | WAIM K05 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.089094 | 0.0038531 | 848 | 55772 | Unplanned | Lightning
1017 |  | 35085 | WAIM - Waimauku | Northern | WAIM K06 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.028906 | 0.0016374 | 373 | 18095 | Unplanned | Lightning
1018 |  | 35085 | WAIM - Waimauku | Northern | WAIM K08 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.094816 | 0.002163 | 677 | 59354 | Unplanned | Lightning
1019 |  | 35085 | WAIM - Waimauku | Northern | WAIM K09 | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 0.034892 | 0.0065496 | 2050 | 21842 | Unplanned | Lightning
1020 |  | 35085 | WAIM - Waimauku | Northern | WAIM LS | 2024-06-17 | 45460.2944 | 2024-06-17 | 45460.4667 | 7.8274e-05 | 4.79e-06 | 1 | 49 | Unplanned | Lightning
1021 |  | 35089 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-06-17 | 45460.4375 | 2024-06-17 | 45460.7188 | 0.22733 | 0.00059905 | 375 | 142308 | Planned | Planned
1022 |  | 35090 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-17 | 45460.5639 | 2024-06-18 | 45461.1042 | 0.049508 | 9.5845e-05 | 60 | 30992 | Unplanned | Third party interference
1023 |  | 35091 | HOBV K07 - K07 CDC HOBSONVILLE #2 | Northern | HOBV K07 | 2024-06-17 | 45460.6687 | 2024-06-17 | 45460.6722 | 7.1883e-05 | 1.4373e-05 | 9 | 45 | Unplanned | Third party interference
1024 |  | 35092 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-17 | 45460.875 | 2024-06-18 | 45461.2306 | 0.13168 | 0.00025719 | 161 | 82432 | Planned | Planned
1025 |  | 35093 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-06-18 | 45461.3542 | 2024-06-18 | 45461.691 | 0.1606 | 0.00035464 | 222 | 100536 | Planned | Planned
1026 |  | 35094 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-06-18 | 45461.5007 | 2024-06-18 | 45461.5833 | 0.0076039 | 6.3896e-05 | 40 | 4760 | Planned | Planned
1027 |  | 35095 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-18 | 45461.6111 | 2024-06-18 | 45461.6215 | 2.3962e-05 | 1.597e-06 | 1 | 15 | Unplanned | Other Cause | Outage caused by Tap Operation
1028 |  | 35096 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2024-06-18 | 45461.4604 | 2024-06-18 | 45461.6104 | 0.023809 | 0.00011022 | 69 | 14904 | Planned | Planned
1029 |  | 35097 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | AVON K03 | 2024-06-18 | 45461.6771 | 2024-06-18 | 45461.6826 | 0.0021086 | 0.00026358 | 165 | 1320 | Unplanned | Wildlife
1030 |  | 35100 | ONEH K09 - K09 - GREY ST | Auckland | ONEH K09 | 2024-06-18 | 45461.9375 | 2024-06-19 | 45462.1826 | 0.18158 | 0.00051438 | 322 | 113666 | Planned | Planned
1031 |  | 35101 | ONEH K12 - K12 - SELWYN ST SOUTH + LS | Auckland | ONEH K12 | 2024-06-18 | 45461.966 | 2024-06-19 | 45462.1542 | 0.046494 | 0.0001885 | 118 | 29105 | Planned | Planned
1032 |  | 35103 | MILF K02 - K02 INGA ROAD | Northern | MILF K02 | 2024-06-18 | 45461.9174 | 2024-06-19 | 45462.0042 | 0.040136 | 0.00032109 | 201 | 25125 | Unplanned | Defective equipment
1033 |  | 35104 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-06-18 | 45461.9583 | 2024-06-19 | 45462.1049 | 0.010449 | 4.9521e-05 | 31 | 6541 | Planned | Planned
1034 |  | 35106 | RIVE K09 - K09 KUMEU | Northern | WAIM K05 | 2024-06-18 | 45461.8806 | 2024-06-18 | 45461.8965 | 0.0029904 | 0.00059429 | 372 | 1872 | Unplanned | Human error
1035 |  | 35106 | RIVE K09 - K09 KUMEU | Northern | WAIM K06 | 2024-06-18 | 45461.8806 | 2024-06-18 | 45461.8965 | 0.00093931 | 0.0003131 | 196 | 588 | Unplanned | Human error
1036 |  | 35106 | RIVE K09 - K09 KUMEU | Northern | WAIM K08 | 2024-06-18 | 45461.8806 | 2024-06-18 | 45461.8965 | 0.013451 | 0.00094248 | 590 | 8420 | Unplanned | Human error
1037 |  | 35108 | MILF K02 - K02 INGA ROAD | Northern | MILF K02 | 2024-06-19 | 45462.1813 | 2024-06-19 | 45462.3083 | 0.00058467 | 3.194e-06 | 2 | 366 | Unplanned | Cause unknown
1038 |  | 35109 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-06-19 | 45462.334 | 2024-06-19 | 45462.7007 | 0.15267 | 0.00028913 | 181 | 95568 | Planned | Planned
1039 |  | 35110 | RBEA K06 - K06 VIPOND RD | Northern | RBEA K06 | 2024-06-19 | 45462.3333 | 2024-06-19 | 45462.7715 | 0.36644 | 0.00081151 | 459 | 229387 | Planned | Planned
1040 |  | 35111 | ORAK K04 - K04 HAWERA RD | Auckland | ORAK K04 | 2024-06-19 | 45462.0854 | 2024-06-19 | 45462.234 | 0.27452 | 0.0021917 | 1021 | 171847 | Unplanned | Defective equipment
1041 |  | 35112 | NCOT K01 - K01 EXMOUTH | Northern | NCOT K01 | 2024-06-19 | 45462.3542 | 2024-06-19 | 45462.7243 | 0.13368 | 0.0002508 | 157 | 83681 | Planned | Planned
1042 |  | 35113 | REMU K12 - K12 PEACH PARADE | Auckland | REMU K12 | 2024-06-19 | 45462.3965 | 2024-06-19 | 45462.7701 | 0.25267 | 0.00046965 | 294 | 158172 | Planned | Planned
1043 |  | 35114 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-06-19 | 45462.0299 | 2024-06-19 | 45462.4097 | 0.0017476 | 3.194e-06 | 2 | 1094 | Unplanned | Cause unknown
1044 |  | 35115 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2024-06-19 | 45462.6694 | 2024-06-19 | 45462.8125 | 0.00032908 | 1.597e-06 | 1 | 206 | Unplanned | Defective equipment
1045 |  | 35116 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-06-19 | 45462.6188 | 2024-06-19 | 45462.7931 | 0.0044106 | 1.757e-05 | 11 | 2761 | Unplanned | Vegetation
1046 |  | 35117 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-19 | 45462.75 | 2024-06-19 | 45462.7812 | 0.00014377 | 3.195e-06 | 2 | 90 | Unplanned | Defective equipment
1047 |  | 35118 | CHEV K09 - K09 PREMIER AVE | Auckland | CHEV K09 | 2024-06-20 | 45463.0417 | 2024-06-20 | 45463.1139 | 0.018441 | 0.00017732 | 111 | 11544 | Planned | Planned
1048 |  | 35119 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-06-20 | 45463.3125 | 2024-06-20 | 45463.6174 | 0.057505 | 0.00013099 | 82 | 35998 | Unplanned | Vegetation
1049 |  | 35120 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2024-06-20 | 45463.3569 | 2024-06-20 | 45463.7104 | 0.20246 | 0.00039777 | 249 | 126741 | Planned | Planned
1050 |  | 35121 | RBEA K05 - K05 JELAS RD | Northern | RBEA K05 | 2024-06-20 | 45463.375 | 2024-06-20 | 45463.6917 | 0.051374 | 0.00011502 | 72 | 32160 | Planned | Planned
1051 |  | 35122 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-06-20 | 45463.4028 | 2024-06-20 | 45463.6944 | 0.00067093 | 1.597e-06 | 1 | 420 | Planned | Planned
1052 |  | 35124 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-06-20 | 45463.5618 | 2024-06-20 | 45463.6687 | 0.0022141 | 1.4377e-05 | 9 | 1386 | Unplanned | Cause unknown
1053 |  | 35125 | GHIT K08 - K08 BERNARD MAGNUS LN | Northern | GHIT K08 | 2024-06-20 | 45463.8431 | 2024-06-20 | 45463.8625 | 0.0011182 | 3.9936e-05 | 25 | 700 | Unplanned | Cause unknown
1054 |  | 35126 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-06-20 | 45463.8014 | 2024-06-20 | 45463.8854 | 0.00057988 | 4.792e-06 | 3 | 363 | Unplanned | Cause unknown
1055 |  | 35127 | TPAP K11 - K11 NZ RIBBON | Auckland | TPAP K11 | 2024-06-20 | 45463.9174 | 2024-06-21 | 45464.1771 | 0.027483 | 7.3482e-05 | 46 | 17204 | Planned | Planned
1056 |  | 35129 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-06-21 | 45464.3951 | 2024-06-23 | 45466.2792 | 0.14859 | 0.00095689 | 412 | 93019 | Unplanned | Third party interference
1057 |  | 35130 | GINN K13 - K13 MELLING ST | Auckland | GINN K13 | 2024-06-21 | 45464.4882 | 2024-06-21 | 45464.5306 | 0.14178 | 0.0023243 | 1455 | 88755 | Unplanned | Defective equipment
1058 |  | 35132 | NSBT71 - TP SILVERDALE 2782 - KAUKAPAKAPA H01 (71) | Northern | KKAP K03 | 2024-06-21 | 45464.3972 | 2024-06-21 | 45464.5722 | 0.029789 | 0.00011821 | 74 | 18648 | Planned | Planned
1059 |  | 35133 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-06-21 | 45464.4 | 2024-06-21 | 45464.6222 | 0.041157 | 0.0001294 | 81 | 25764 | Planned | Planned
1060 |  | 35134 | FBSH K05 - K05 WISTERIA LANE | Auckland | FBSH K05 | 2024-06-21 | 45464.7278 | 2024-06-21 | 45464.7792 | 0.00035464 | 4.792e-06 | 3 | 222 | Unplanned | Third party interference
1061 |  | 35135 | TAKA K12 - K12 MILL RD | Auckland | MKAU K19 | 2024-06-21 | 45464.7292 | 2024-06-21 | 45464.7944 | 0.00045048 | 4.792e-06 | 3 | 282 | Unplanned | Cause unknown
1062 |  | 35136 | TPAP K11 - K11 NZ RIBBON | Auckland | TPAP K11 | 2024-06-21 | 45464.9174 | 2024-06-22 | 45465.1562 | 0.0093419 | 2.7157e-05 | 17 | 5848 | Planned | Planned
1063 |  | 35137 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-06-21 | 45464.9167 | 2024-06-23 | 45466.9972 | 0.024015 | 0.00013898 | 44 | 15033 | Planned | Planned
1064 |  | 35138 | BALM K04 - K04 TRURO ROAD | Auckland | BALM K04 | 2024-06-21 | 45464.9444 | 2024-06-22 | 45465.2917 | 0.00079873 | 1.597e-06 | 1 | 500 | Planned | Planned
1065 |  | 35139 | PAPA K01 - K01 SETTLEMENT RD | Auckland | PAPA K01 | 2024-06-22 | 45465.3479 | 2024-06-22 | 45465.4292 | 0.0091582 | 7.8275e-05 | 49 | 5733 | Unplanned | Defective equipment
1066 |  | 35140 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-06-22 | 45465.3965 | 2024-06-22 | 45465.7028 | 0.27334 | 0.00061981 | 388 | 171108 | Planned | Planned
1067 |  | 35141 | BMON K08 - K08 CHELTENHAM | Northern | BMON K08 | 2024-06-22 | 45465.3542 | 2024-06-22 | 45465.691 | 0.0829 | 0.00017093 | 107 | 51895 | Planned | Planned
1068 |  | 35142 | WSWA K15 - K15 GRIFFEN RD | Auckland | WSWA K15 | 2024-06-22 | 45465.4549 | 2024-06-22 | 45465.5729 | 0.080731 | 0.0023291 | 1458 | 50537 | Unplanned | Defective equipment
1069 |  | 35143 | MWEL K12 - K12 AHI CONTAINER DIVISION | Auckland | MWEL K12 | 2024-06-22 | 45465.5153 | 2024-06-22 | 45465.6076 | 0.13101 | 0.0013115 | 821 | 82009 | Unplanned | Defective equipment
1070 |  | 35144 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-22 | 45465.75 | 2024-06-25 | 45468.375 | 0.012077 | 3.195e-06 | 2 | 7560 | Unplanned | Other Cause | Outage on Non-Vector asset
1071 |  | 35145 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-22 | 45465.8958 | 2024-06-22 | 45465.9375 | 0.0086982 | 0.00016134 | 101 | 5445 | Planned | Planned
1072 |  | 35146 | SUNS K11 - K11 PARKWAY DRIVE | Northern | SUNS K11 | 2024-06-23 | 45466.3333 | 2024-06-23 | 45466.7049 | 0.0042732 | 7.987e-06 | 5 | 2675 | Planned | Planned
1073 |  | 35148 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-22 | 45465.6333 | 2024-06-24 | 45467.0833 | 0.010006 | 4.792e-06 | 3 | 6264 | Unplanned | Defective equipment
1074 |  | 35151 | BOMA - Big Omaha | Northern | BOMA K01 | 2024-06-23 | 45466.7972 | 2024-06-23 | 45466.8708 | 0.41883 | 0.0039886 | 2497 | 262185 | Unplanned | Cause unknown
1075 |  | 35151 | BOMA - Big Omaha | Northern | BOMA K04 | 2024-06-23 | 45466.7972 | 2024-06-23 | 45466.8708 | 0.12378 | 0.0015128 | 947 | 77487 | Unplanned | Cause unknown
1076 |  | 35151 | BOMA - Big Omaha | Northern | BOMA K06 | 2024-06-23 | 45466.7972 | 2024-06-23 | 45466.8708 | 0.00016614 | 1.596e-06 | 1 | 104 | Unplanned | Cause unknown
1077 |  | 35152 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2024-06-23 | 45466.8833 | 2024-06-23 | 45466.9083 | 5.7509e-05 | 1.597e-06 | 1 | 36 | Unplanned | Defective equipment
1078 |  | 35153 | GREE K16 - K16 HARRIS ROAD SOUTH | Auckland | GREE K16 | 2024-06-23 | 45466.9424 | 2024-06-24 | 45467.1507 | 0.0038339 | 1.278e-05 | 8 | 2400 | Planned | Planned
1079 |  | 35154 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-06-23 | 45466.9007 | 2024-06-24 | 45467.3965 | 0.10352 | 0.00030192 | 189 | 64802 | Unplanned | Defective equipment
1080 |  | 35156 | CHEV K03 - K03 ACC WESTERN GARDENS | Auckland | CHEV K03 | 2024-06-24 | 45467.2083 | 2024-06-24 | 45467.2556 | 0.01738 | 0.00025559 | 160 | 10880 | Planned | Planned
1081 |  | 35157 | RBEA K05 - K05 JELAS RD | Northern | RBEA K05 | 2024-06-24 | 45467.3799 | 2024-06-27 | 45470.584 | 0.018761 | 0.00028115 | 88 | 11744 | Planned | Planned
1082 |  | 35158 | FORR K08 - K08 GORDON AVE | Northern | FORR K08 | 2024-06-24 | 45467.7007 | 2024-06-24 | 45467.7208 | 0.020801 | 0.0013818 | 865 | 13021 | Unplanned | Third party interference
1083 |  | 35159 | RBEA K05 - K05 JELAS RD | Northern | RBEA K05 | 2024-06-24 | 45467.7153 | 2024-06-24 | 45467.7431 | 0.001917 | 4.7924e-05 | 30 | 1200 | Unplanned | Defective equipment
1084 |  | 35160 | HVAL K06 - K06 CATHERINE ST | Northern | HVAL K06 | 2024-06-24 | 45467.8243 | 2024-06-24 | 45467.9056 | 0.011027 | 9.4251e-05 | 59 | 6903 | Unplanned | Defective equipment
1085 |  | 35161 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-06-24 | 45467.8125 | 2024-06-24 | 45467.9424 | 0.00029873 | 1.597e-06 | 1 | 187 | Planned | Planned
1086 |  | 35162 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-06-25 | 45468.116 | 2024-06-25 | 45468.1646 | 0.013642 | 0.00019489 | 122 | 8540 | Unplanned | Defective equipment
1087 |  | 35163 | CHEV K01 - K01 MOTAT | Auckland | CHEV K01 | 2024-06-25 | 45468.1667 | 2024-06-25 | 45468.2368 | 0.12478 | 0.0015559 | 974 | 78109 | Unplanned | Defective equipment
1088 |  | 35163 | CHEV K01 - K01 MOTAT | Auckland | KING K06 | 2024-06-25 | 45468.1667 | 2024-06-25 | 45468.2368 | 0.047668 | 0.00059585 | 373 | 29840 | Unplanned | Defective equipment
1089 |  | 35164 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-06-25 | 45468.241 | 2024-06-25 | 45468.4722 | 0.064812 | 0.00040256 | 126 | 40572 | Unplanned | Defective equipment
1090 |  | 35165 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-25 | 45468.3069 | 2024-06-25 | 45468.3083 | 6.39e-06 | 3.195e-06 | 2 | 4 | Planned | Planned
1091 |  | 35166 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-25 | 45468.3174 | 2024-06-25 | 45468.3194 | 9.585e-06 | 3.195e-06 | 2 | 6 | Planned | Planned
1092 |  | 35167 | BUSH K08 - K08 UNITY DR | Northern | BUSH K08 | 2024-06-25 | 45468.3333 | 2024-06-25 | 45468.6562 | 0.064384 | 0.00028115 | 88 | 40304 | Planned | Planned
1093 |  | 35168 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-06-25 | 45468.3854 | 2024-06-25 | 45468.5208 | 0.00062301 | 3.195e-06 | 2 | 390 | Planned | Planned
1094 |  | 35169 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2024-06-25 | 45468.375 | 2024-06-25 | 45468.6958 | 0.084873 | 0.00018371 | 115 | 53130 | Planned | Planned
1095 |  | 35170 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-25 | 45468.3417 | 2024-06-25 | 45468.3444 | 6.39e-06 | 1.597e-06 | 1 | 4 | Planned | Planned
1096 |  | 35171 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-06-25 | 45468.3972 | 2024-06-25 | 45468.7097 | 0.0064697 | 1.4375e-05 | 9 | 4050 | Planned | Planned
1097 |  | 35172 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-06-25 | 45468.3549 | 2024-06-25 | 45468.6924 | 0.077637 | 0.00015975 | 100 | 48600 | Planned | Planned
1098 |  | 35173 | WSWA K06 - K06 ROSKILL RIPPLE | Auckland | WSWA K06 | 2024-06-25 | 45468.6083 | 2024-06-25 | 45468.7486 | 0.13641 | 0.0025256 | 1581 | 85392 | Unplanned | Third party interference
1099 |  | 35174 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-06-25 | 45468.5437 | 2024-06-25 | 45468.6215 | 0.0023259 | 2.0767e-05 | 13 | 1456 | Unplanned | Third party interference
1100 |  | 35175 | TAKA K13 - K13 COSGROVE RD | Auckland | TAKA K13 | 2024-06-25 | 45468.709 | 2024-06-25 | 45468.7722 | 0.20638 | 0.002623 | 1642 | 129192 | Unplanned | Third party interference
1101 |  | 35176 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-06-25 | 45468.9264 | 2024-06-25 | 45468.9875 | 0.0016869 | 1.9169e-05 | 12 | 1056 | Unplanned | Cause unknown
1102 |  | 35177 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-26 | 45469.3583 | 2024-06-26 | 45469.6181 | 0.023898 | 6.3893e-05 | 40 | 14960 | Planned | Planned
1103 |  | 35178 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-06-26 | 45469.3792 | 2024-06-26 | 45469.7396 | 0.009949 | 1.9168e-05 | 12 | 6228 | Planned | Planned
1104 |  | 35180 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-06-26 | 45469.6979 | 2024-06-26 | 45469.7688 | 0.0008147 | 7.987e-06 | 5 | 510 | Unplanned | Defective equipment
1105 |  | 35181 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-06-26 | 45469.8403 | 2024-06-27 | 45470.0625 | 0.024026 | 7.5077e-05 | 47 | 15040 | Unplanned | Defective equipment
1106 |  | 35182 | PARN K13 - K13 PARNELL RD 258 | Auckland | PARN K13 | 2024-06-27 | 45470.0069 | 2024-06-27 | 45470.1813 | 0.022454 | 8.9458e-05 | 56 | 14056 | Planned | Planned
1107 |  | 35183 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-26 | 45469.7646 | 2024-06-27 | 45470.7604 | 0.046334 | 9.5846e-05 | 60 | 29005 | Unplanned | Defective equipment
1108 |  | 35184 | BMON K02 - K02 NARROW NECK | Northern | BMON K02 | 2024-06-27 | 45470.3438 | 2024-06-27 | 45470.6833 | 0.17342 | 0.00035464 | 222 | 108558 | Planned | Planned
1109 |  | 35185 | PONS K08 - K08 VERMONT ST | Auckland | FREE K62 | 2024-06-27 | 45470.3701 | 2024-06-27 | 45470.6424 | 0.22032 | 0.0018515 | 1159 | 137921 | Unplanned | Defective equipment
1110 |  | 35185 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2024-06-27 | 45470.3701 | 2024-06-27 | 45470.6424 | 0.35631 | 0.0016853 | 1055 | 223048 | Unplanned | Defective equipment
1111 |  | 35186 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-06-27 | 45470.375 | 2024-06-27 | 45470.6861 | 0.058684 | 0.00013099 | 82 | 36736 | Planned | Planned
1112 |  | 35187 | NSBT15 - TP SILVERDALE 2742 - MANLY P262 (15) | Northern | MANL K11 | 2024-06-27 | 45470.3653 | 2024-06-27 | 45470.8021 | 0.021598 | 4.1534e-05 | 26 | 13520 | Planned | Planned
1113 |  | 35188 | ORAK K05 - K05 GODDEN CRES | Auckland | ORAK K05 | 2024-06-27 | 45470.3757 | 2024-06-27 | 45470.5215 | 0.024489 | 0.00011661 | 73 | 15330 | Planned | Planned
1114 |  | 35189 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2024-06-27 | 45470.4097 | 2024-06-27 | 45470.7639 | 0.087988 | 0.00017253 | 108 | 55080 | Planned | Planned
1115 |  | 35190 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-06-27 | 45470.4201 | 2024-06-27 | 45470.5833 | 0.18019 | 0.00076678 | 480 | 112800 | Planned | Planned
1116 |  | 35191 | NLYN K07 - K07 BINSTEAD RD | Northern | NLYN K07 | 2024-06-27 | 45470.5639 | 2024-06-27 | 45470.5653 | 0.002524 | 0.001262 | 790 | 1580 | Unplanned | Human error
1117 |  | 35192 | NEWM K01 - K01 EDUCATIONAL DEPT VIA LS | Auckland | NEWM K01 | 2024-06-28 | 45471.3417 | 2024-06-29 | 45472.1653 | 0.058719 | 0.00058787 | 184 | 36758 | Unplanned | Third party interference
1118 |  | 35193 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-28 | 45471.5333 | 2024-06-28 | 45471.5833 | 0.00011502 | 1.597e-06 | 1 | 72 | Unplanned | Cause unknown
1119 |  | 35196 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-29 | 45472.5188 | 2024-06-29 | 45472.5729 | 0.013083 | 0.00016773 | 105 | 8190 | Unplanned | Defective equipment
1120 |  | 35198 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-06-29 | 45472.8514 | 2024-06-29 | 45472.909 | 0.034496 | 0.00082269 | 515 | 21594 | Unplanned | Third party interference
1121 |  | 35199 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-06-29 | 45472.9556 | 2024-07-01 | 45474.0132 | 0.12005 | 0.0012859 | 651 | 75151 | Unplanned | Third party interference
1122 |  | 35200 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-06-29 | 45472.7868 | 2024-06-30 | 45473.1479 | 0.0016614 | 3.194e-06 | 2 | 1040 | Unplanned | Defective equipment
1123 |  | 35201 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-06-30 | 45473.1743 | 2024-06-30 | 45473.4444 | 0.098804 | 0.00025399 | 159 | 61851 | Unplanned | Third party interference
1124 |  | 35202 | ROSE K12 - K12 SMITH & NEPHEW | Auckland | ROSE K12 | 2024-06-30 | 45473.3715 | 2024-06-30 | 45473.5285 | 0.0097477 | 4.3131e-05 | 27 | 6102 | Planned | Planned
1125 |  | 35203 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-06-30 | 45473.6042 | 2024-06-30 | 45473.6083 | 0.00022045 | 3.6742e-05 | 23 | 138 | Unplanned | Other Cause | Outage caused by Tap Operation
1126 |  | 35204 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-06-30 | 45473.9104 | 2024-07-01 | 45474.0181 | 0.10011 | 0.0014616 | 836 | 62670 | Unplanned | Cause unknown
1127 |  | 35205 | TPAP K11 - K11 NZ RIBBON | Auckland | TPAP K11 | 2024-06-30 | 45473.9167 | 2024-07-01 | 45474.1785 | 0.02763 | 7.3482e-05 | 46 | 17296 | Planned | Planned
1128 |  | 35207 | TORB K11 - K11 BEACH ROAD | Northern | TORB K11 | 2024-07-01 | 45474.3958 | 2024-07-01 | 45474.7569 | 0.0026198 | 6.5496e-05 | 41 | 1640 | Planned | Planned
1129 |  | 35208 | BROW K05 - K05 ARRAN ROAD & LS | Northern | BROW K05 | 2024-07-01 | 45474.3965 | 2024-07-01 | 45474.7069 | 0.06855 | 0.00015336 | 96 | 42912 | Planned | Planned
1130 |  | 35209 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-07-01 | 45474.3972 | 2024-07-01 | 45474.6826 | 0.0045959 | 1.1182e-05 | 7 | 2877 | Planned | Planned
1131 |  | 35210 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-07-01 | 45474.3993 | 2024-07-01 | 45474.7007 | 0.0006933 | 1.597e-06 | 1 | 434 | Planned | Planned
1132 |  | 35211 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-07-01 | 45474.3958 | 2024-07-01 | 45474.6188 | 0.11794 | 0.00036742 | 230 | 73830 | Planned | Planned
1133 |  | 35212 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-07-01 | 45474.5417 | 2024-07-05 | 45478.6833 | 0.0095272 | 1.597e-06 | 1 | 5964 | Unplanned | Defective equipment
1134 |  | 35213 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-07-01 | 45474.8382 | 2024-07-02 | 45475.2083 | 0.10302 | 0.00019329 | 121 | 64493 | Planned | Planned
1135 |  | 35214 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-07-01 | 45474.8229 | 2024-07-01 | 45474.9271 | 0.00023962 | 1.597e-06 | 1 | 150 | Unplanned | Defective equipment
1136 |  | 35215 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-07-01 | 45474.8924 | 2024-07-01 | 45474.9 | 0.00021086 | 1.917e-05 | 12 | 132 | Unplanned | Other Cause | Outage caused by Tap Operation
1137 |  | 35216 | TPAP K11 - K11 NZ RIBBON | Auckland | TPAP K11 | 2024-07-01 | 45474.9174 | 2024-07-02 | 45475.1667 | 0.0097493 | 2.7157e-05 | 17 | 6103 | Planned | Planned
1138 |  | 35217 | LIVE K11 - K11 SAPPHIRE APARTMENTS | Auckland | LIVE K11 | 2024-07-01 | 45474.9167 | 2024-07-02 | 45475.2646 | 0.002377 | 4.792e-06 | 3 | 1488 | Planned | Planned
1139 |  | 35218 | RBEA K02 - K02 FANTAIL COURT + LS | Northern | RBEA K02 | 2024-07-02 | 45475.3438 | 2024-07-02 | 45475.6576 | 0.071483 | 0.00015815 | 99 | 44748 | Planned | Planned
1140 |  | 35219 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-07-02 | 45475.3444 | 2024-07-02 | 45475.6875 | 0.005524 | 1.1182e-05 | 7 | 3458 | Planned | Planned
1141 |  | 35221 | CHEV K04 - K04 MOA RD | Auckland | CHEV K04 | 2024-07-02 | 45475.3771 | 2024-07-02 | 45475.7188 | 0.21378 | 0.00043451 | 272 | 133824 | Planned | Planned
1142 |  | 35222 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-07-02 | 45475.375 | 2024-07-02 | 45475.6667 | 0.14962 | 0.00035623 | 223 | 93660 | Planned | Planned
1143 |  | 35223 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-07-02 | 45475.3486 | 2024-07-02 | 45475.7111 | 0.0033355 | 6.39e-06 | 4 | 2088 | Unplanned | Defective equipment
1144 |  | 35224 | AVON K06 - K06 NEW NORTH RD. 1225 | Auckland | AVON K06 | 2024-07-02 | 45475.4722 | 2024-07-02 | 45475.5708 | 0.072362 | 0.00050959 | 319 | 45298 | Planned | Planned
1145 |  | 35225 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-07-02 | 45475.7812 | 2024-07-02 | 45475.7917 | 2.3962e-05 | 1.597e-06 | 1 | 15 | Unplanned | Other Cause | Outage caused by Tap Operation
1146 |  | 35226 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-07-03 | 45476.2083 | 2024-07-03 | 45476.291 | 0.12299 | 0.0010336 | 647 | 76993 | Planned | Planned
1147 |  | 35227 | BRIC K04 - K04 LINKS RD | Northern | BRIC K04 | 2024-07-03 | 45476.3556 | 2024-07-03 | 45476.6792 | 0.021588 | 4.6326e-05 | 29 | 13514 | Planned | Planned
1148 |  | 35228 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-07-03 | 45476.4167 | 2024-07-03 | 45476.5882 | 0.0011837 | 4.792e-06 | 3 | 741 | Planned | Planned
1149 |  | 35229 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-07-03 | 45476.4646 | 2024-07-03 | 45476.684 | 0.028582 | 0.00041055 | 256 | 17892 | Unplanned | Defective equipment
1150 |  | 35231 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-07-03 | 45476.6618 | 2024-07-03 | 45476.6806 | 0.00017253 | 6.39e-06 | 4 | 108 | Unplanned | Vegetation
1151 |  | 35232 | GREE K16 - K16 HARRIS ROAD SOUTH | Auckland | GREE K16 | 2024-07-03 | 45476.9167 | 2024-07-04 | 45477.1743 | 0.0047413 | 1.278e-05 | 8 | 2968 | Planned | Planned
1152 |  | 35233 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-07-04 | 45477.1931 | 2024-07-04 | 45477.2278 | 0.040328 | 0.0013371 | 837 | 25245 | Unplanned | Cause unknown
1153 |  | 35234 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-07-04 | 45477.209 | 2024-07-04 | 45477.2688 | 0.088886 | 0.0010336 | 647 | 55642 | Planned | Planned
1154 |  | 35235 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-07-04 | 45477.209 | 2024-07-05 | 45478.0938 | 0.084651 | 0.00038659 | 148 | 52991 | Unplanned | Defective equipment
1155 |  | 35236 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-07-04 | 45477.3542 | 2024-07-04 | 45477.7264 | 0.014511 | 2.7156e-05 | 17 | 9084 | Planned | Planned
1156 |  | 35237 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-07-04 | 45477.3333 | 2024-07-04 | 45477.7361 | 0.10776 | 0.00034186 | 122 | 67456 | Planned | Planned
1157 |  | 35238 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-07-04 | 45477.3958 | 2024-07-04 | 45477.6285 | 0.0010703 | 3.195e-06 | 2 | 670 | Planned | Planned
1158 |  | 35239 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-07-04 | 45477.4153 | 2024-07-04 | 45477.7792 | 0.027623 | 5.2716e-05 | 33 | 17292 | Planned | Planned
1159 |  | 35240 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-07-04 | 45477.7014 | 2024-07-04 | 45477.8 | 0.00045368 | 3.195e-06 | 2 | 284 | Unplanned | Cause unknown
1160 |  | 35241 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-07-04 | 45477.8382 | 2024-07-05 | 45478.0236 | 0.026444 | 9.9042e-05 | 62 | 16554 | Unplanned | Cause unknown
1161 |  | 35242 | CHEV K04 - K04 MOA RD | Auckland | CHEV K04 | 2024-07-05 | 45478.2083 | 2024-07-05 | 45478.2701 | 0.064831 | 0.00072844 | 456 | 40584 | Planned | Planned
1162 |  | 35243 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-07-05 | 45478.2556 | 2024-07-05 | 45478.3674 | 0.016406 | 0.0012172 | 762 | 10270 | Unplanned | Vegetation
1163 |  | 35244 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-07-05 | 45478.3347 | 2024-07-05 | 45478.8097 | 0.036058 | 5.2716e-05 | 33 | 22572 | Planned | Planned
1164 |  | 35245 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-07-05 | 45478.3542 | 2024-07-05 | 45478.7306 | 0.0051949 | 9.585e-06 | 6 | 3252 | Planned | Planned
1165 |  | 35247 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-07-05 | 45478.3778 | 2024-07-05 | 45478.6319 | 0.020463 | 5.591e-05 | 35 | 12810 | Planned | Planned
1166 |  | 35248 | AVON K08 - K08 NEW WINDSOR RD. | Auckland | AVON K08 | 2024-07-05 | 45478.3958 | 2024-07-05 | 45478.6021 | 0.02562 | 8.6263e-05 | 54 | 16038 | Planned | Planned
1167 |  | 35249 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-07-05 | 45478.4167 | 2024-07-05 | 45478.6181 | 0.019016 | 0.00030671 | 128 | 11904 | Planned | Planned
1168 |  | 35250 | AVON K02 - K02 ST JUDE ST.(PENSIONER FLATS) | Auckland | AVON K02 | 2024-07-05 | 45478.9604 | 2024-07-06 | 45479.2014 | 0.081485 | 0.00023483 | 147 | 51009 | Planned | Planned
1169 |  | 35252 | MCEN K01 - K01 MANGERE BRIDGE | Auckland | MCEN K01 | 2024-07-06 | 45479.3854 | 2024-07-06 | 45479.7472 | 0.43528 | 0.00083547 | 523 | 272483 | Planned | Planned
1170 |  | 35253 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-07-06 | 45479.4479 | 2024-07-06 | 45479.4625 | 0.0040927 | 0.00019489 | 122 | 2562 | Unplanned | Vegetation
1171 |  | 35254 | KKAP K06 - K06 PEAK RD | Northern | KKAP K06 | 2024-07-06 | 45479.5458 | 2024-07-07 | 45480.3194 | 0.050914 | 0.00042014 | 263 | 31872 | Unplanned | Third party interference
1172 |  | 35255 | ROSE K15 - K15 BEATRIX ROAD VIA LOCAL | Auckland | ROSE K15 | 2024-07-06 | 45479.6458 | 2024-07-07 | 45480.5312 | 0.022404 | 1.7572e-05 | 11 | 14025 | Unplanned | Cause unknown
1173 |  | 35261 | PARN K13 - K13 PARNELL RD 258 | Auckland | PARN K13 | 2024-07-07 | 45480.6215 | 2024-07-07 | 45480.7292 | 0.00049521 | 3.195e-06 | 2 | 310 | Unplanned | Defective equipment
1174 |  | 35262 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-07-07 | 45480.3313 | 2024-07-07 | 45480.6653 | 0.0023051 | 4.792e-06 | 3 | 1443 | Unplanned | Defective equipment
1175 |  | 35263 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-07-08 | 45481.2826 | 2024-07-08 | 45481.3882 | 0.0012141 | 7.987e-06 | 5 | 760 | Unplanned | Cause unknown
1176 |  | 35264 | CHEV K11 - K11 ANDY MILLER LTD VIA LS | Auckland | CHEV K11 | 2024-07-08 | 45481.4174 | 2024-07-08 | 45481.5903 | 0.13604 | 0.00054633 | 342 | 85158 | Planned | Planned
1177 |  | 35265 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-07 | 45480.7194 | 2024-07-08 | 45481.4271 | 0.0016278 | 1.597e-06 | 1 | 1019 | Unplanned | Cause unknown
1178 |  | 35266 | MARA K08 - K08 MARAETAI DR | Auckland | MARA K08 | 2024-07-08 | 45481.5556 | 2024-07-08 | 45481.6042 | 0.0045847 | 6.5496e-05 | 41 | 2870 | Unplanned | Third party interference
1179 |  | 35268 | SIMP K07 - K07 BABICH RD | Northern | SIMP K07 | 2024-07-08 | 45481.5833 | 2024-07-08 | 45481.5972 | 3.1949e-05 | 1.597e-06 | 1 | 20 | Unplanned | Other Cause | Outage caused by Tap Operation
1180 |  | 35269 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2024-07-08 | 45481.8146 | 2024-07-09 | 45482.4062 | 0.09517 | 0.0020112 | 1186 | 59576 | Unplanned | Defective equipment
1181 |  | 35269 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K11 | 2024-07-08 | 45481.8146 | 2024-07-09 | 45482.4062 | 0.00012141 | 1.596e-06 | 1 | 76 | Unplanned | Defective equipment
1182 |  | 35272 | MANU K11 - K11 MANUREWA CENTRAL | Auckland | MANU K11 | 2024-07-08 | 45481.925 | 2024-07-09 | 45482.1368 | 0.0097445 | 3.1949e-05 | 20 | 6100 | Planned | Planned
1183 |  | 35273 | PONS K19 - K19 NORFOLK ST | Auckland | PONS K19 | 2024-07-08 | 45481.9375 | 2024-07-09 | 45482.1368 | 0.018339 | 6.3898e-05 | 40 | 11480 | Planned | Planned
1184 |  | 35274 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-07-08 | 45481.9708 | 2024-07-09 | 45482.0181 | 0.0008179 | 1.278e-05 | 8 | 512 | Unplanned | Cause unknown
1185 |  | 35275 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-07-09 | 45482.3333 | 2024-07-09 | 45482.6681 | 0.23946 | 0.0004968 | 311 | 149902 | Planned | Planned
1186 |  | 35276 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-07-09 | 45482.3368 | 2024-07-09 | 45482.5903 | 0.025655 | 7.0284e-05 | 44 | 16060 | Planned | Planned
1187 |  | 35277 | NLYN K04 - K04 RATA ST | Northern | NLYN K04 | 2024-07-09 | 45482.3333 | 2024-07-09 | 45482.6875 | 0.029329 | 5.7509e-05 | 36 | 18360 | Planned | Planned
1188 |  | 35278 | BIRK K02 - K02 DOMAIN ROAD | Northern | BIRK K02 | 2024-07-09 | 45482.375 | 2024-07-09 | 45482.7639 | 0.1282 | 0.00023962 | 150 | 80250 | Planned | Planned
1189 |  | 35278 | BIRK K02 - K02 DOMAIN ROAD | Northern | WAIR K12 | 2024-07-09 | 45482.375 | 2024-07-09 | 45482.7639 | 0.063834 | 0.00011821 | 74 | 39960 | Planned | Planned
1190 |  | 35279 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-07-09 | 45482.375 | 2024-07-09 | 45482.7146 | 0.0039058 | 7.987e-06 | 5 | 2445 | Planned | Planned
1191 |  | 35280 | RDAL K11 - K11 HUGH GREEN DR | Northern | RDAL K11 | 2024-07-09 | 45482.3958 | 2024-07-09 | 45482.5507 | 0.09084 | 0.00040735 | 255 | 56865 | Planned | Planned
1192 |  | 35281 | TRIA K10 - K10 WEST | Northern | TRIA K10 | 2024-07-09 | 45482.3854 | 2024-07-09 | 45482.7646 | 0.034889 | 6.3898e-05 | 40 | 21840 | Planned | Planned
1193 |  | 35282 | WAIR K11 - K11 PORANA ROAD | Northern | WAIR K11 | 2024-07-09 | 45482.5132 | 2024-07-09 | 45482.8056 | 0.018831 | 4.4729e-05 | 28 | 11788 | Unplanned | Defective equipment
1194 |  | 35283 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-07-09 | 45482.5667 | 2024-07-12 | 45485.6972 | 0.021655 | 2.0766e-05 | 9 | 13556 | Unplanned | Defective equipment
1195 |  | 35284 | WAIA K04 - K04 CAPRICORN PLACE | Northern | WAIA K04 | 2024-07-09 | 45482.6646 | 2024-07-09 | 45482.7819 | 0.10124 | 0.00059905 | 375 | 63375 | Unplanned | Defective equipment
1196 |  | 35285 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-07-09 | 45482.7389 | 2024-07-09 | 45482.8083 | 0.052818 | 0.0028067 | 1225 | 33064 | Unplanned | Cause unknown
1197 |  | 35286 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-07-10 | 45483.3333 | 2024-07-10 | 45483.7 | 0.3416 | 0.00064697 | 405 | 213840 | Planned | Planned
1198 |  | 35287 | AVON K08 - K08 NEW WINDSOR RD. | Auckland | AVON K08 | 2024-07-10 | 45483.391 | 2024-07-10 | 45483.4986 | 0.045536 | 0.00030352 | 190 | 28505 | Planned | Planned
1199 |  | 35288 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-07-10 | 45483.4167 | 2024-07-10 | 45483.6319 | 0.097733 | 0.00031789 | 199 | 61180 | Planned | Planned
1200 |  | 35289 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-10 | 45483.4021 | 2024-07-10 | 45483.4785 | 0.00017572 | 1.597e-06 | 1 | 110 | Unplanned | Cause unknown
1201 |  | 35290 | NSBT73 - BIRKDALE H07 - BALMAIN P154 (73) | Northern | BIRK K10 | 2024-07-10 | 45483.5597 | 2024-07-11 | 45484.0625 | 0.20409 | 0.00034186 | 214 | 127758 | Unplanned | Third party interference
1202 |  | 35291 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-07-10 | 45483.7736 | 2024-07-10 | 45483.8604 | 0.10009 | 0.0023403 | 1465 | 62655 | Unplanned | Defective equipment
1203 |  | 35291 | BIRK K05 - K05 FORDHAM STREET | Northern | BLMN K04 | 2024-07-10 | 45483.7736 | 2024-07-10 | 45483.8604 | 0.010673 | 0.001778 | 1113 | 6681 | Unplanned | Defective equipment
1204 |  | 35292 | MKIN K11 - K11 THE AVENUE | Northern | MKIN K11 | 2024-07-10 | 45483.9375 | 2024-07-11 | 45484.1097 | 0.028118 | 0.00011342 | 71 | 17602 | Unplanned | Defective equipment
1205 |  | 35293 | HBUR K03 - K03 MAHARA AVE + LS | Northern | HBUR K03 | 2024-07-11 | 45484.3333 | 2024-07-11 | 45484.7007 | 0.056619 | 0.00010703 | 67 | 35443 | Planned | Planned
1206 |  | 35294 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-07-11 | 45484.3771 | 2024-07-11 | 45484.5049 | 0.0011757 | 6.39e-06 | 4 | 736 | Planned | Planned
1207 |  | 35295 | ORAK K11 - K11 KOHIMARAMA RD | Auckland | ORAK K11 | 2024-07-11 | 45484.3771 | 2024-07-11 | 45484.7764 | 0.16442 | 0.00028595 | 179 | 102925 | Planned | Planned
1208 |  | 35296 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-07-11 | 45484.375 | 2024-07-11 | 45484.625 | 0.043131 | 0.0001198 | 75 | 27000 | Planned | Planned
1209 |  | 35297 | NLYN K07 - K07 BINSTEAD RD | Northern | NLYN K07 | 2024-07-11 | 45484.3861 | 2024-07-11 | 45484.4132 | 0.046633 | 0.0012652 | 792 | 29192 | Unplanned | Wildlife
1210 |  | 35298 | MILF K02 - K02 INGA ROAD | Northern | MILF K02 | 2024-07-11 | 45484.366 | 2024-07-11 | 45484.4903 | 0.057475 | 0.00032109 | 201 | 35979 | Planned | Planned
1211 |  | 35299 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2024-07-11 | 45484.6569 | 2024-07-11 | 45484.7118 | 0.037633 | 0.0041151 | 2576 | 23558 | Unplanned | Defective equipment
1212 |  | 35300 | FORR K09 - K09 MATIPO ROAD | Northern | ECOA K01 | 2024-07-11 | 45484.9056 | 2024-07-11 | 45484.9069 | 0.0034729 | 0.0017364 | 1087 | 2174 | Unplanned | Defective equipment
1213 |  | 35300 | FORR K09 - K09 MATIPO ROAD | Northern | FORR K09 | 2024-07-11 | 45484.9056 | 2024-07-11 | 45484.9069 | 0.00095848 | 0.00047924 | 300 | 600 | Unplanned | Defective equipment
1214 |  | 35301 | PONS K19 - K19 NORFOLK ST | Auckland | PONS K19 | 2024-07-12 | 45485.125 | 2024-07-12 | 45485.25 | 0.011789 | 6.5496e-05 | 41 | 7380 | Planned | Planned
1215 |  | 35302 | MWEL K11 - K11 MT. WELLINGTON H'WAY NORTH | Auckland | MNAB K06 | 2024-07-12 | 45485.1771 | 2024-07-12 | 45485.2743 | 0.019781 | 0.0028259 | 1769 | 12383 | Unplanned | Defective equipment
1216 |  | 35302 | MWEL K11 - K11 MT. WELLINGTON H'WAY NORTH | Auckland | MWEL K01 | 2024-07-12 | 45485.1771 | 2024-07-12 | 45485.2743 | 0.11465 | 0.0018658 | 1168 | 71770 | Unplanned | Defective equipment
1217 |  | 35303 | NLYN K07 - K07 BINSTEAD RD | Northern | NLYN K07 | 2024-07-12 | 45485.3507 | 2024-07-12 | 45485.4986 | 0.086138 | 0.0012652 | 792 | 53922 | Unplanned | Defective equipment
1218 |  | 35304 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-07-12 | 45485.3556 | 2024-07-12 | 45485.6708 | 0.01378 | 3.035e-05 | 19 | 8626 | Planned | Planned
1219 |  | 35305 | SPUR K07 - K07 PINEVALLEY | Northern | SPUR K07 | 2024-07-12 | 45485.375 | 2024-07-12 | 45485.7431 | 0.0024297 | 4.791e-06 | 3 | 1521 | Planned | Planned
1220 |  | 35305 | SPUR K07 - K07 PINEVALLEY | Northern | SPUR K09 | 2024-07-12 | 45485.375 | 2024-07-12 | 45485.7431 | 0.036406 | 6.8682e-05 | 43 | 22790 | Planned | Planned
1221 |  | 35306 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-12 | 45485.4167 | 2024-07-12 | 45485.4792 | 0.0044569 | 4.9521e-05 | 31 | 2790 | Planned | Planned
1222 |  | 35307 | WSWA K06 - K06 ROSKILL RIPPLE | Auckland | WSWA K06 | 2024-07-12 | 45485.4708 | 2024-07-12 | 45485.5625 | 0.0084346 | 6.3898e-05 | 40 | 5280 | Unplanned | Third party interference
1223 |  | 35308 | NLYN - New Lynn | Northern | NLYN K01 | 2024-07-12 | 45485.4833 | 2024-07-12 | 45485.4868 | 0.0054505 | 0.0013626 | 853 | 3412 | Unplanned | Defective equipment
1224 |  | 35308 | NLYN - New Lynn | Northern | NLYN K02 | 2024-07-12 | 45485.4833 | 2024-07-12 | 45485.4868 | 0.0034186 | 0.00085464 | 535 | 2140 | Unplanned | Defective equipment
1225 |  | 35308 | NLYN - New Lynn | Northern | NLYN K04 | 2024-07-12 | 45485.4833 | 2024-07-12 | 45485.4868 | 0.0084266 | 0.0016853 | 1055 | 5275 | Unplanned | Defective equipment
1226 |  | 35308 | NLYN - New Lynn | Northern | NLYN K05 | 2024-07-12 | 45485.4833 | 2024-07-12 | 45485.4868 | 0.0046646 | 0.00093292 | 584 | 2920 | Unplanned | Defective equipment
1227 |  | 35308 | NLYN - New Lynn | Northern | NLYN K10 | 2024-07-12 | 45485.4833 | 2024-07-12 | 45485.4868 | 0.0068132 | 0.0013626 | 853 | 4265 | Unplanned | Defective equipment
1228 |  | 35308 | NLYN - New Lynn | Northern | NLYN K11 | 2024-07-12 | 45485.4833 | 2024-07-12 | 45485.4868 | 0.01119 | 0.0022381 | 1401 | 7005 | Unplanned | Defective equipment
1229 |  | 35310 | CHEV K11 - K11 ANDY MILLER LTD VIA LS | Auckland | CHEV K11 | 2024-07-12 | 45485.9174 | 2024-07-13 | 45486.2354 | 0.14512 | 0.00032269 | 200 | 90844 | Planned | Planned
1230 |  | 35311 | BMON K01 - K01 ACHILLES CRESCENT | Northern | BMON K01 | 2024-07-12 | 45485.9958 | 2024-07-13 | 45486.4535 | 0.28553 | 0.0015623 | 978 | 178742 | Unplanned | Third party interference
1231 |  | 35312 | MALB K20 - K20 FOWLER AVE | Auckland | MALB K20 | 2024-07-13 | 45486.3826 | 2024-07-13 | 45486.7063 | 0.084068 | 0.00018211 | 114 | 52626 | Planned | Planned
1232 |  | 35314 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2024-07-13 | 45486.3368 | 2024-07-13 | 45486.7139 | 0.11016 | 0.00020288 | 127 | 68961 | Planned | Planned
1233 |  | 35315 | BUSH K04 - K04 UNSWORTH DRIVE | Northern | BUSH K02 | 2024-07-13 | 45486.3403 | 2024-07-13 | 45486.6438 | 0.0034904 | 7.987e-06 | 5 | 2185 | Planned | Planned
1234 |  | 35317 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K03 | 2024-07-13 | 45486.3528 | 2024-07-13 | 45486.6868 | 0.010767 | 0.0021534 | 1348 | 6740 | Unplanned | Defective equipment
1235 |  | 35317 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-07-13 | 45486.3528 | 2024-07-13 | 45486.6868 | 0.12949 | 0.0045927 | 1957 | 81063 | Unplanned | Defective equipment
1236 |  | 35318 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-07-13 | 45486.4132 | 2024-07-13 | 45486.5938 | 0.001246 | 4.792e-06 | 3 | 780 | Unplanned | Wildlife
1237 |  | 35319 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-07-13 | 45486.7382 | 2024-07-13 | 45486.7965 | 0.15852 | 0.0043707 | 2736 | 99232 | Unplanned | Defective equipment
1238 |  | 35321 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2024-07-13 | 45486.9097 | 2024-07-13 | 45486.966 | 0.017727 | 0.00021884 | 137 | 11097 | Unplanned | Cause unknown
1239 |  | 35323 | SAND K08 - K08 DUNCAN AVE | Auckland | SAND K08 | 2024-07-13 | 45486.9931 | 2024-07-14 | 45487.684 | 0.094771 | 0.00036742 | 128 | 59326 | Unplanned | Third party interference
1240 |  | 35324 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-07-14 | 45487.2889 | 2024-07-14 | 45487.4576 | 0.0023291 | 9.585e-06 | 6 | 1458 | Unplanned | Cause unknown
1241 |  | 35325 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-07-14 | 45487.5049 | 2024-07-14 | 45487.8083 | 0.10544 | 0.00054791 | 236 | 66003 | Unplanned | Defective equipment
1242 |  | 35326 | KING K09 - K09 381 NEW NORTH RD | Auckland | KING K09 | 2024-07-14 | 45487.9799 | 2024-07-18 | 45491.2118 | 0.16376 | 0.00092653 | 290 | 102510 | Planned | Planned
1243 |  | 35327 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-07-15 | 45488.0722 | 2024-07-15 | 45488.2049 | 0.037293 | 0.0009505 | 595 | 23345 | Unplanned | Cause unknown
1244 |  | 35329 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-07-15 | 45488.1813 | 2024-07-15 | 45488.6556 | 0.12274 | 0.0014345 | 898 | 76832 | Unplanned | Defective equipment
1245 |  | 35330 | BMON K03 - K03 CENTRAL | Northern | BMON K03 | 2024-07-15 | 45488.2931 | 2024-07-15 | 45488.3347 | 0.010687 | 0.00021885 | 137 | 6690 | Planned | Planned
1246 |  | 35331 | CLEN K05 - K05 WEYMOUTH EAST | Auckland | CLEN K05 | 2024-07-15 | 45488.3403 | 2024-07-15 | 45488.4743 | 0.013874 | 7.1886e-05 | 45 | 8685 | Unplanned | Defective equipment
1247 |  | 35332 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-07-15 | 45488.5104 | 2024-07-15 | 45488.5521 | 0.0028754 | 4.7924e-05 | 30 | 1800 | Unplanned | Defective equipment
1248 |  | 35333 | MKIN K07 - K07 LANDING DRIVE | Northern | MKIN K07 | 2024-07-15 | 45488.3403 | 2024-07-16 | 45489.0972 | 0.0020735 | 4.79e-06 | 3 | 1298 | Unplanned | Defective equipment
1249 |  | 35334 | JAME K10 - K10 HOGANS ROAD | Northern | JAME K10 | 2024-07-15 | 45488.8299 | 2024-07-16 | 45489.1507 | 0.0014761 | 3.195e-06 | 2 | 924 | Unplanned | Third party interference
1250 |  | 35336 | MANU K11 - K11 MANUREWA CENTRAL | Auckland | MANU K11 | 2024-07-15 | 45488.9187 | 2024-07-16 | 45489.1826 | 0.012141 | 3.1949e-05 | 20 | 7600 | Planned | Planned
1251 |  | 35337 | NEWT K19 - K19 JOHN ANDREW | Auckland | NEWT K19 | 2024-07-15 | 45488.8368 | 2024-07-16 | 45489.1194 | 0.058986 | 0.00022205 | 131 | 36925 | Unplanned | Cause unknown
1252 |  | 35339 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-07-16 | 45489 | 2024-07-16 | 45489.1535 | 0.0025511 | 0.00013898 | 44 | 1597 | Unplanned | Defective equipment
1253 |  | 35340 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-07-15 | 45488.8507 | 2024-07-16 | 45489.2965 | 0.066499 | 0.00021245 | 133 | 41628 | Unplanned | Cause unknown
1254 |  | 35342 | TATA K05 - K05 PARAMOUNT DR | Northern | TATA K05 | 2024-07-16 | 45489.334 | 2024-07-16 | 45489.7201 | 0.051515 | 9.2653e-05 | 58 | 32248 | Planned | Planned
1255 |  | 35343 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-16 | 45489.375 | 2024-07-16 | 45489.6903 | 0.03046 | 6.7091e-05 | 42 | 19068 | Planned | Planned
1256 |  | 35344 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-07-16 | 45489.3569 | 2024-07-16 | 45489.6854 | 0.11787 | 0.00024921 | 156 | 73788 | Planned | Planned
1257 |  | 35345 | RANU K09 - K09 ALIDADE PLACE | Northern | RANU K09 | 2024-07-16 | 45489.3958 | 2024-07-16 | 45489.5417 | 0.02147 | 0.00010224 | 64 | 13440 | Planned | Planned
1258 |  | 35346 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-07-16 | 45489.3958 | 2024-07-16 | 45489.4507 | 0.0005048 | 6.39e-06 | 4 | 316 | Unplanned | Defective equipment
1259 |  | 35347 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-07-16 | 45489.4181 | 2024-07-16 | 45489.4417 | 0.0063547 | 0.0001869 | 117 | 3978 | Planned | Planned
1260 |  | 35348 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2024-07-16 | 45489.8028 | 2024-07-17 | 45490.3181 | 0.11972 | 0.00016134 | 101 | 74942 | Unplanned | Defective equipment
1261 |  | 35349 | ONEH K12 - K12 - SELWYN ST SOUTH + LS | Auckland | ONEH K12 | 2024-07-16 | 45489.9757 | 2024-07-17 | 45490.0104 | 0.0071087 | 0.00014217 | 89 | 4450 | Unplanned | Defective equipment
1262 |  | 35350 | BIRK K02 - K02 DOMAIN ROAD | Northern | BIRK K02 | 2024-07-17 | 45490.2118 | 2024-07-18 | 45491.2417 | 0.16396 | 0.00039138 | 233 | 102639 | Planned | Planned
1263 |  | 35351 | SABU K07 - K07 AWAROA RD | Northern | SABU K07 | 2024-07-17 | 45490.334 | 2024-07-17 | 45490.7118 | 0.049534 | 9.1055e-05 | 57 | 31008 | Planned | Planned
1264 |  | 35352 | GINN K08 - K08 EAST VIEW RD | Auckland | GINN K08 | 2024-07-17 | 45490.2799 | 2024-07-17 | 45490.5451 | 0.0073228 | 1.917e-05 | 12 | 4584 | Unplanned | Defective equipment
1265 |  | 35353 | TRIA K04 - K04 WAIMUMU RD | Northern | TRIA K04 | 2024-07-17 | 45490.3958 | 2024-07-17 | 45490.5257 | 0.021508 | 0.00011502 | 72 | 13464 | Planned | Planned
1266 |  | 35354 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-07-17 | 45490.4653 | 2024-07-17 | 45490.5083 | 0.00049521 | 7.987e-06 | 5 | 310 | Unplanned | Defective equipment
1267 |  | 35355 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-07-17 | 45490.4896 | 2024-07-17 | 45490.5403 | 0.0016326 | 2.2364e-05 | 14 | 1022 | Unplanned | Defective equipment
1268 |  | 35356 | JAME K08 - K08 GLENFIELD ROAD | Northern | BIRK K02 | 2024-07-17 | 45490.309 | 2024-07-17 | 45490.3667 | 0.0093483 | 0.00024601 | 154 | 5852 | Unplanned | Human error
1269 |  | 35356 | JAME K08 - K08 GLENFIELD ROAD | Northern | JAME K08 | 2024-07-17 | 45490.309 | 2024-07-17 | 45490.3667 | 0.0053339 | 0.00016933 | 53 | 3339 | Unplanned | Human error
1270 |  | 35357 | NSBT95 - RANUI H02 - SWANSON H07 (95) | Northern | SWAN K09 | 2024-07-17 | 45490.2729 | 2024-07-18 | 45491.0312 | 0.085806 | 0.00034186 | 214 | 53714 | Planned | Planned
1271 |  | 35358 | WOOD K05 - K05 FAIRDENE AVE | Northern | WOOD K05 | 2024-07-17 | 45490.9764 | 2024-07-18 | 45491.966 | 0.064833 | 0.00031151 | 140 | 40585 | Planned | Planned
1272 |  | 35359 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2024-07-18 | 45491.1104 | 2024-07-18 | 45491.1813 | 0.098525 | 0.0040719 | 2458 | 61676 | Unplanned | Defective equipment
1273 |  | 35361 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-07-18 | 45491.3542 | 2024-07-18 | 45491.6035 | 0.0028674 | 7.987e-06 | 5 | 1795 | Planned | Planned
1274 |  | 35362 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-07-18 | 45491.3542 | 2024-07-18 | 45491.7 | 0.27605 | 0.00055431 | 347 | 172806 | Planned | Planned
1275 |  | 35364 | SAND K18 - K18 SANDRINGHAM RD EXTN - SOUTH | Auckland | SAND K18 | 2024-07-18 | 45491.3542 | 2024-07-18 | 45491.7229 | 0.051743 | 9.7445e-05 | 61 | 32391 | Planned | Planned
1276 |  | 35365 | HOWI K10 - K10 FINNERTY AVE | Auckland | HOWI K10 | 2024-07-18 | 45491.375 | 2024-07-18 | 45491.625 | 0.018403 | 5.1119e-05 | 32 | 11520 | Planned | Planned
1277 |  | 35366 | SHOW K05 - K05 LITTEN RD | Auckland | SHOW K05 | 2024-07-18 | 45491.3979 | 2024-07-18 | 45491.7972 | 0.054194 | 9.425e-05 | 59 | 33925 | Planned | Planned
1278 |  | 35367 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-07-18 | 45491.4208 | 2024-07-18 | 45491.65 | 0.0060576 | 3.834e-05 | 12 | 3792 | Unplanned | Defective equipment
1279 |  | 35368 | OREW K10 - K10 HATFIELDS | Northern | OREW K10 | 2024-07-18 | 45491.65 | 2024-07-18 | 45491.7674 | 0.021328 | 0.0001262 | 79 | 13351 | Unplanned | Defective equipment
1280 |  | 35369 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-07-18 | 45491.7681 | 2024-07-18 | 45491.8007 | 0.0012764 | 2.7157e-05 | 17 | 799 | Unplanned | Third party interference
1281 |  | 35370 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-07-18 | 45491.716 | 2024-07-18 | 45491.7847 | 0.00079074 | 7.987e-06 | 5 | 495 | Unplanned | Cause unknown
1282 |  | 35371 | TRIA K02 - K02 SOUTH | Northern | TRIA K02 | 2024-07-18 | 45491.875 | 2024-07-19 | 45492.0444 | 0.0019489 | 7.987e-06 | 5 | 1220 | Planned | Planned
1283 |  | 35372 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-07-18 | 45491.9167 | 2024-07-19 | 45492.2319 | 0.09559 | 0.00021246 | 133 | 59839 | Planned | Planned
1284 |  | 35373 | HOBV K10 - K10 OREIL AVENUE | Northern | HOBV K10 | 2024-07-18 | 45491.9174 | 2024-07-19 | 45492.041 | 0.066253 | 0.00037221 | 233 | 41474 | Planned | Planned
1285 |  | 35374 | KEEL K12 - K12 STURGES RD | Northern | KEEL K12 | 2024-07-19 | 45492.0729 | 2024-07-19 | 45492.2639 | 0.070728 | 0.00025719 | 161 | 44275 | Unplanned | Third party interference
1286 |  | 35375 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2024-07-19 | 45492.3542 | 2024-07-19 | 45492.7451 | 0.37234 | 0.00066135 | 414 | 233082 | Planned | Planned
1287 |  | 35376 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-07-19 | 45492.375 | 2024-07-19 | 45492.434 | 0.00040735 | 4.792e-06 | 3 | 255 | Planned | Planned
1288 |  | 35377 | WGAT K12 - K12 ALLOWAY | Northern | WGAT K12 | 2024-07-19 | 45492.3972 | 2024-07-19 | 45492.5951 | 0.020943 | 7.3483e-05 | 46 | 13110 | Planned | Planned
1289 |  | 35378 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2024-07-19 | 45492.5479 | 2024-07-19 | 45492.6208 | 0.007548 | 0.0015096 | 945 | 4725 | Unplanned | Cause unknown
1290 |  | 35378 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K06 | 2024-07-19 | 45492.5479 | 2024-07-19 | 45492.6208 | 0.040282 | 0.00053196 | 333 | 25216 | Unplanned | Cause unknown
1291 |  | 35379 | BMON K03 - K03 CENTRAL | Northern | BMON K03 | 2024-07-19 | 45492.5431 | 2024-07-19 | 45492.5708 | 0.0047381 | 0.00022045 | 138 | 2966 | Planned | Planned
1292 |  | 35380 | PAPA K09 - K09 LAURIE AVE | Auckland | PAPA K09 | 2024-07-19 | 45492.9313 | 2024-07-20 | 45493.2396 | 0.28442 | 0.00064058 | 401 | 178044 | Planned | Planned
1293 |  | 35381 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-07-19 | 45492.9694 | 2024-07-20 | 45493.1243 | 0.079967 | 0.00050002 | 313 | 50059 | Unplanned | Cause unknown
1294 |  | 35382 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-07-20 | 45493.2674 | 2024-07-20 | 45493.3958 | 0.00059106 | 3.194e-06 | 2 | 370 | Unplanned | Vegetation
1295 |  | 35383 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-07-20 | 45493.5771 | 2024-07-20 | 45493.7715 | 0.036678 | 0.00013099 | 82 | 22960 | Unplanned | Vegetation
1296 |  | 35384 | TPAP K20 - K20 O/H CHURCH STREET | Auckland | TPAP K20 | 2024-07-20 | 45493.4056 | 2024-07-20 | 45493.5868 | 0.00083387 | 3.195e-06 | 2 | 522 | Planned | Planned
1297 |  | 35385 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | AVON K03 | 2024-07-20 | 45493.8035 | 2024-07-21 | 45494.0132 | 0.047278 | 0.00015655 | 98 | 29596 | Unplanned | Defective equipment
1298 |  | 35386 | MILF K04 - K04 ALMA RD | Northern | MILF K04 | 2024-07-20 | 45493.8993 | 2024-07-21 | 45494.1979 | 0.072125 | 0.00016773 | 105 | 45150 | Planned | Planned
1299 |  | 35387 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2024-07-20 | 45493.8278 | 2024-07-21 | 45494.1514 | 0.0029777 | 6.39e-06 | 4 | 1864 | Unplanned | Cause unknown
1300 |  | 35388 | TATA K05 - K05 PARAMOUNT DR | Northern | TATA K05 | 2024-07-21 | 45494.3542 | 2024-07-21 | 45494.6736 | 0.015431 | 3.3547e-05 | 21 | 9660 | Planned | Planned
1301 |  | 35389 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-07-21 | 45494.6125 | 2024-07-21 | 45494.75 | 0.015815 | 7.9873e-05 | 50 | 9900 | Unplanned | Defective equipment
1302 |  | 35390 | FBSH K05 - K05 WISTERIA LANE | Auckland | FBSH K05 | 2024-07-21 | 45494.8382 | 2024-07-22 | 45495.525 | 0.33473 | 0.0049585 | 3101 | 209537 | Unplanned | Cause unknown
1303 |  | 35391 | PONS K16 - K16 PARAWAI CRES | Auckland | PONS K16 | 2024-07-21 | 45494.9375 | 2024-07-22 | 45495.0819 | 0.010965 | 5.2716e-05 | 33 | 6864 | Planned | Planned
1304 |  | 35392 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-07-21 | 45494.9375 | 2024-07-22 | 45495.1944 | 0.0681 | 0.0001869 | 117 | 42630 | Planned | Planned
1305 |  | 35393 | NEWM K02 - K02 BROADWAY CENTRE | Auckland | NEWM K02 | 2024-07-21 | 45494.9583 | 2024-07-22 | 45495.05 | 0.015556 | 0.00097445 | 328 | 9738 | Planned | Planned
1306 |  | 35394 | KING K12 - K12 GT NORTH RD | Auckland | KING K12 | 2024-07-21 | 45494.9792 | 2024-07-22 | 45495.0396 | 0.031131 | 0.00035783 | 224 | 19488 | Planned | Planned
1307 |  | 35395 | GINN K02 - K02 PADDINGTON ST | Auckland | GINN K02 | 2024-07-22 | 45495.0833 | 2024-07-22 | 45495.1736 | 0.017652 | 0.00013578 | 85 | 11050 | Planned | Planned
1308 |  | 35396 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-07-22 | 45495.3785 | 2024-07-22 | 45495.3889 | 4.7924e-05 | 3.195e-06 | 2 | 30 | Planned | Planned
1309 |  | 35397 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-07-22 | 45495.4639 | 2024-07-22 | 45495.4688 | 5.5911e-05 | 7.987e-06 | 5 | 35 | Planned | Planned
1310 |  | 35398 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-07-22 | 45495.4792 | 2024-07-22 | 45495.5299 | 0.00034984 | 4.792e-06 | 3 | 219 | Unplanned | Defective equipment
1311 |  | 35399 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-07-22 | 45495.5486 | 2024-07-22 | 45495.5556 | 4.7924e-05 | 4.792e-06 | 3 | 30 | Planned | Planned
1312 |  | 35400 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-07-22 | 45495.625 | 2024-07-22 | 45495.6319 | 0.00046326 | 4.6326e-05 | 29 | 290 | Planned | Planned
1313 |  | 35401 | LIVE K11 - K11 SAPPHIRE APARTMENTS | Auckland | LIVE K11 | 2024-07-22 | 45495.9583 | 2024-07-23 | 45496.0569 | 0.0024952 | 1.7572e-05 | 11 | 1562 | Planned | Planned
1314 |  | 35402 | MNAB K02 - K02 GAVIN ST WEST | Auckland | MNAB K02 | 2024-07-22 | 45495.9792 | 2024-07-23 | 45496.1556 | 0.090483 | 0.00035623 | 223 | 56642 | Planned | Planned
1315 |  | 35402 | MNAB K02 - K02 GAVIN ST WEST | Auckland | MNAB K33 | 2024-07-22 | 45495.9792 | 2024-07-23 | 45496.1556 | 0.076282 | 0.00030032 | 188 | 47752 | Planned | Planned
1316 |  | 35404 | RBEA K06 - K06 VIPOND RD | Northern | RBEA K06 | 2024-07-23 | 45496.3333 | 2024-07-23 | 45496.7257 | 0.062277 | 0.00011022 | 69 | 38985 | Planned | Planned
1317 |  | 35405 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-07-23 | 45496.3542 | 2024-07-23 | 45496.6125 | 0.087355 | 0.00023483 | 147 | 54684 | Planned | Planned
1318 |  | 35406 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-07-23 | 45496.375 | 2024-07-23 | 45496.7069 | 0.10843 | 0.00022684 | 142 | 67876 | Planned | Planned
1319 |  | 35407 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-07-23 | 45496.3806 | 2024-07-23 | 45496.3889 | 0.00013419 | 1.1182e-05 | 7 | 84 | Planned | Planned
1320 |  | 35408 | CLEN K11 - K11 SHARLAND | Auckland | CLEN K11 | 2024-07-23 | 45496.4153 | 2024-07-23 | 45496.5222 | 0.0088563 | 5.7509e-05 | 36 | 5544 | Planned | Planned
1321 |  | 35409 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-07-23 | 45496.3333 | 2024-07-23 | 45496.6458 | 0.0043131 | 9.585e-06 | 6 | 2700 | Planned | Planned
1322 |  | 35410 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-07-23 | 45496.4028 | 2024-07-23 | 45496.6736 | 0.0062301 | 1.5975e-05 | 10 | 3900 | Planned | Planned
1323 |  | 35411 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-07-23 | 45496.3556 | 2024-07-23 | 45496.6611 | 0.0042173 | 9.585e-06 | 6 | 2640 | Planned | Planned
1324 |  | 35412 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-07-23 | 45496.4597 | 2024-07-23 | 45496.4681 | 5.7509e-05 | 4.792e-06 | 3 | 36 | Planned | Planned
1325 |  | 35413 | MARA K10 - K10 OMANA BEACH RD | Auckland | MARA K10 | 2024-07-23 | 45496.5417 | 2024-07-23 | 45496.5486 | 1.5975e-05 | 1.597e-06 | 1 | 10 | Planned | Planned
1326 |  | 35414 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-23 | 45496.625 | 2024-07-23 | 45496.6319 | 0.00038339 | 3.8339e-05 | 24 | 240 | Planned | Planned
1327 |  | 35415 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-07-23 | 45496.9375 | 2024-07-24 | 45497.2153 | 0.046646 | 0.00011661 | 73 | 29200 | Planned | Planned
1328 |  | 35416 | LIVE K11 - K11 SAPPHIRE APARTMENTS | Auckland | LIVE K11 | 2024-07-23 | 45496.9583 | 2024-07-24 | 45497.0528 | 0.052358 | 0.00038499 | 241 | 32776 | Planned | Planned
1329 |  | 35417 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-07-24 | 45497.0312 | 2024-07-24 | 45497.0458 | 0.00063739 | 3.0352e-05 | 19 | 399 | Unplanned | Defective equipment
1330 |  | 35418 | NEWM K06 - K06 CARLTON GORE ROAD (111) | Auckland | NEWM K06 | 2024-07-24 | 45497.0833 | 2024-07-24 | 45497.1889 | 0.0067988 | 4.4729e-05 | 28 | 4256 | Planned | Planned
1331 |  | 35419 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-24 | 45497.375 | 2024-07-24 | 45497.7069 | 0.01069 | 2.2364e-05 | 14 | 6692 | Planned | Planned
1332 |  | 35420 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2024-07-24 | 45497.3354 | 2024-07-24 | 45497.7278 | 0.076718 | 0.00013578 | 85 | 48025 | Planned | Planned
1333 |  | 35421 | TATA K05 - K05 PARAMOUNT DR | Northern | TATA K05 | 2024-07-24 | 45497.3771 | 2024-07-24 | 45497.5813 | 0.00046965 | 1.597e-06 | 1 | 294 | Planned | Planned
1334 |  | 35423 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-07-24 | 45497.3799 | 2024-07-24 | 45497.6326 | 0.00027317 | 1.7571e-05 | 11 | 171 | Planned | Planned
1335 |  | 35424 | HVAL K06 - K06 CATHERINE ST | Northern | HVAL K06 | 2024-07-24 | 45497.5021 | 2024-07-24 | 45497.6653 | 0.0097605 | 4.1534e-05 | 26 | 6110 | Unplanned | Defective equipment
1336 |  | 35425 | MKIN K11 - K11 THE AVENUE | Northern | MKIN K11 | 2024-07-24 | 45497.6514 | 2024-07-24 | 45497.6917 | 0.00050799 | 9.585e-06 | 6 | 318 | Planned | Planned
1337 |  | 35427 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-07-24 | 45497.6479 | 2024-07-24 | 45497.7028 | 0.001262 | 1.5973e-05 | 10 | 790 | Unplanned | Defective equipment
1338 |  | 35428 | HOBV K11 - K11 TRIG RD +LS | Northern | HOBV K11 | 2024-07-24 | 45497.6542 | 2024-07-24 | 45497.75 | 0.0037476 | 2.7156e-05 | 17 | 2346 | Unplanned | Cause unknown
1339 |  | 35429 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-07-24 | 45497.7618 | 2024-07-24 | 45497.8299 | 0.0061055 | 6.2301e-05 | 39 | 3822 | Unplanned | Cause unknown
1340 |  | 35430 | PAKU K02 - K02 GRASSWAYS AVE | Auckland | PAKU K02 | 2024-07-24 | 45497.9167 | 2024-07-25 | 45498.2069 | 0.032013 | 0.00053355 | 167 | 20040 | Planned | Planned
1341 |  | 35431 | WSWA K08 - K08 COMMODORE DRIVE | Auckland | WSWA K08 | 2024-07-24 | 45497.9583 | 2024-07-25 | 45498.0431 | 0.010329 | 8.4665e-05 | 53 | 6466 | Planned | Planned
1342 |  | 35432 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-07-24 | 45497.9792 | 2024-07-25 | 45498.2153 | 0.049425 | 0.00014537 | 91 | 30940 | Planned | Planned
1343 |  | 35434 | GINN K13 - K13 MELLING ST | Auckland | GINN K13 | 2024-07-25 | 45498.1042 | 2024-07-25 | 45498.1875 | 0.021278 | 0.00017732 | 111 | 13320 | Planned | Planned
1344 |  | 35435 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-07-25 | 45498.341 | 2024-07-25 | 45498.6861 | 0.098407 | 0.0010895 | 386 | 61602 | Planned | Planned
1345 |  | 35436 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-07-25 | 45498.3542 | 2024-07-25 | 45498.6632 | 0.029857 | 6.7087e-05 | 42 | 18690 | Planned | Planned
1346 |  | 35437 | HPOI K06 - K06 WISELEY RD | Northern | HPOI K06 | 2024-07-25 | 45498.3903 | 2024-07-25 | 45498.6007 | 0.015973 | 5.2716e-05 | 33 | 9999 | Planned | Planned
1347 |  | 35438 | HOBV K04 - K04 ELIZABETH DR | Northern | HOBV K04 | 2024-07-25 | 45498.3542 | 2024-07-25 | 45498.7674 | 0.15169 | 0.00026838 | 168 | 94960 | Planned | Planned
1348 |  | 35439 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-07-25 | 45498.375 | 2024-07-25 | 45498.6528 | 0.066454 | 0.00016614 | 104 | 41600 | Planned | Planned
1349 |  | 35440 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-07-25 | 45498.3958 | 2024-07-25 | 45498.5569 | 0.024032 | 0.00034026 | 213 | 15044 | Unplanned | Defective equipment
1350 |  | 35441 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-25 | 45498.3785 | 2024-07-25 | 45498.6181 | 0.00023323 | 2.2363e-05 | 14 | 146 | Planned | Planned
1351 |  | 35442 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-07-25 | 45498.3958 | 2024-07-25 | 45498.4792 | 0.0001917 | 1.597e-06 | 1 | 120 | Unplanned | Cause unknown
1352 |  | 35444 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-07-25 | 45498.6854 | 2024-07-25 | 45498.7375 | 0.00011981 | 1.597e-06 | 1 | 75 | Unplanned | Defective equipment
1353 |  | 35445 | NLYN K07 - K07 BINSTEAD RD | Northern | NLYN K07 | 2024-07-25 | 45498.7625 | 2024-07-25 | 45498.9611 | 0.11428 | 0.0012636 | 791 | 71538 | Unplanned | Cause unknown
1354 |  | 35446 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-07-25 | 45498.5569 | 2024-07-27 | 45500.4708 | 0.020457 | 5.9105e-05 | 37 | 12806 | Unplanned | Defective equipment
1355 |  | 35448 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-07-25 | 45498.9375 | 2024-07-26 | 45499.0417 | 0.0040735 | 2.7157e-05 | 17 | 2550 | Planned | Planned
1356 |  | 35449 | MKAU K16 - K16 BAKERFIELD PLACE (VIA LST2) | Auckland | MKAU K16 | 2024-07-25 | 45498.9583 | 2024-07-26 | 45499.2188 | 0.0018451 | 7.987e-06 | 4 | 1155 | Planned | Planned
1357 |  | 35450 | GINN K13 - K13 MELLING ST | Auckland | GINN K13 | 2024-07-25 | 45498.9583 | 2024-07-26 | 45499.0451 | 0.023163 | 0.00018531 | 116 | 14500 | Planned | Planned
1358 |  | 35452 | SJOH K09 - K09 168 NORMAN LESSER DR | Auckland | SJOH K09 | 2024-07-26 | 45499.0833 | 2024-07-26 | 45499.1611 | 0.022186 | 0.00019808 | 124 | 13888 | Planned | Planned
1359 |  | 35453 | FREE K20 - K20 FRANKLIN RD 44 | Auckland | FREE K65 | 2024-07-26 | 45499.2604 | 2024-07-26 | 45499.4618 | 0.090582 | 0.0028307 | 886 | 56704 | Unplanned | Third party interference
1360 |  | 35453 | FREE K20 - K20 FRANKLIN RD 44 | Auckland | PONS K08 | 2024-07-26 | 45499.2604 | 2024-07-26 | 45499.4618 | 0.20391 | 0.0020767 | 972 | 127644 | Unplanned | Third party interference
1361 |  | 35454 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-07-26 | 45499.3542 | 2024-07-26 | 45499.6986 | 0.044371 | 8.9458e-05 | 56 | 27776 | Planned | Planned
1362 |  | 35455 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-26 | 45499.375 | 2024-07-26 | 45499.5354 | 0.0045799 | 2.0768e-05 | 13 | 2867 | Planned | Planned
1363 |  | 35456 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-26 | 45499.3799 | 2024-07-26 | 45499.4653 | 0.0001885 | 2.0767e-05 | 13 | 118 | Planned | Planned
1364 |  | 35457 | NLYN K02 - K02 TITIRANGI RD | Northern | NLYN K02 | 2024-07-26 | 45499.6764 | 2024-07-27 | 45500.1021 | 0.21643 | 0.00085464 | 535 | 135481 | Unplanned | Third party interference
1365 |  | 35459 | MANU K22 - K22 HOLMES RD | Auckland | MANU K22 | 2024-07-27 | 45500.0417 | 2024-07-27 | 45500.1 | 0.003623 | 4.3131e-05 | 27 | 2268 | Planned | Planned
1366 |  | 35460 | PARN K11 - K11 BONNICI MOTORS VIA SW/STN | Auckland | PARN K11 | 2024-07-27 | 45500.3028 | 2024-07-27 | 45500.5583 | 0.070454 | 0.00021566 | 127 | 44104 | Unplanned | Defective equipment
1367 |  | 35461 | WEST K17 - K17 ABBATOIR LNE SW/STN VIA LS | Auckland | WEST K17 | 2024-07-27 | 45500.3181 | 2024-07-27 | 45500.7028 | 0.002655 | 4.792e-06 | 3 | 1662 | Planned | Planned
1368 |  | 35462 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-07-27 | 45500.3333 | 2024-07-27 | 45500.6458 | 0.00071886 | 1.597e-06 | 1 | 450 | Planned | Planned
1369 |  | 35464 | SNEL K08 - K08 ALGIES BAY | Northern | SNEL K08 | 2024-07-27 | 45500.8917 | 2024-07-28 | 45501.0257 | 0.10976 | 0.0005687 | 356 | 68708 | Unplanned | Third party interference
1370 |  | 35465 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-07-27 | 45500.6694 | 2024-07-27 | 45500.8438 | 0.0040096 | 1.5974e-05 | 10 | 2510 | Unplanned | Cause unknown
1371 |  | 35467 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-07-28 | 45501.2215 | 2024-07-28 | 45501.3313 | 0.0010096 | 6.389e-06 | 4 | 632 | Unplanned | Cause unknown
1372 |  | 35470 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-07-28 | 45501.4799 | 2024-07-28 | 45501.625 | 0.0036726 | 1.7572e-05 | 11 | 2299 | Unplanned | Cause unknown
1373 |  | 35471 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-07-28 | 45501.609 | 2024-07-28 | 45501.7792 | 0.1177 | 0.0029745 | 1862 | 73681 | Unplanned | Defective equipment
1374 |  | 35472 | ROSE K08 - K08 HONAN PL PHIPPS ROCOL | Auckland | ROSE K08 | 2024-07-28 | 45501.7 | 2024-07-28 | 45501.7896 | 0.26192 | 0.0020304 | 1271 | 163959 | Unplanned | Defective equipment
1375 |  | 35473 | GINN K01 - K01 WEST TAMAKI RD VIA LS | Auckland | GINN K01 | 2024-07-28 | 45501.9583 | 2024-07-29 | 45502.0431 | 0.015981 | 0.00013099 | 82 | 10004 | Planned | Planned
1376 |  | 35474 | GINN K01 - K01 WEST TAMAKI RD VIA LS | Auckland | GINN K01 | 2024-07-29 | 45502.0833 | 2024-07-29 | 45502.1701 | 0.035144 | 0.00028115 | 176 | 22000 | Planned | Planned
1377 |  | 35475 | BMON K02 - K02 NARROW NECK | Northern | BMON K02 | 2024-07-29 | 45502.191 | 2024-07-29 | 45502.2083 | 7.9873e-05 | 3.195e-06 | 2 | 50 | Planned | Planned
1378 |  | 35476 | MANL K02 - K02 STANMORE BAY | Northern | MANL K02 | 2024-07-29 | 45502.3958 | 2024-07-29 | 45502.5236 | 0.00029393 | 1.597e-06 | 1 | 184 | Planned | Planned
1379 |  | 35477 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-29 | 45502.3854 | 2024-07-29 | 45502.4653 | 0.00041055 | 3.1949e-05 | 20 | 257 | Planned | Planned
1380 |  | 35479 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-07-29 | 45502.5139 | 2024-07-29 | 45502.566 | 0.055858 | 0.0028914 | 1810 | 34967 | Unplanned | Vegetation
1381 |  | 35480 | TAKA K08 - K08 GRAHAM RD | Auckland | MANU K08 | 2024-07-29 | 45502.7778 | 2024-07-29 | 45502.8319 | 0.026949 | 0.0015879 | 994 | 16870 | Unplanned | Defective equipment
1382 |  | 35480 | TAKA K08 - K08 GRAHAM RD | Auckland | MANU K23 | 2024-07-29 | 45502.7778 | 2024-07-29 | 45502.8319 | 2.5559e-05 | 1.598e-06 | 1 | 16 | Unplanned | Defective equipment
1383 |  | 35480 | TAKA K08 - K08 GRAHAM RD | Auckland | TAKA K08 | 2024-07-29 | 45502.7778 | 2024-07-29 | 45502.8319 | 0.050464 | 0.00064697 | 405 | 31590 | Unplanned | Defective equipment
1384 |  | 35481 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2024-07-29 | 45502.7965 | 2024-07-29 | 45502.8139 | 0.0027556 | 0.00011022 | 69 | 1725 | Unplanned | Defective equipment
1385 |  | 35482 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-07-29 | 45502.7764 | 2024-07-29 | 45502.8313 | 0.020066 | 0.000254 | 159 | 12561 | Unplanned | Cause unknown
1386 |  | 35484 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-07-29 | 45502.8479 | 2024-07-29 | 45502.9424 | 0.0034761 | 2.5557e-05 | 16 | 2176 | Unplanned | Cause unknown
1387 |  | 35485 | NEWT K12 - K12 AIR NEW ZEALAND COMPUTER CENTRE | Auckland | NEWT K12 | 2024-07-29 | 45502.9583 | 2024-07-30 | 45503.0493 | 0.019462 | 0.00014856 | 93 | 12183 | Planned | Planned
1388 |  | 35486 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-07-30 | 45503.1667 | 2024-07-30 | 45503.2257 | 0.0045144 | 0.00017252 | 108 | 2826 | Planned | Planned
1389 |  | 35487 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2024-07-30 | 45503.3562 | 2024-07-30 | 45503.7417 | 0.22874 | 0.00041214 | 258 | 143190 | Planned | Planned
1390 |  | 35488 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2024-07-30 | 45503.3854 | 2024-07-30 | 45503.6701 | 0.13246 | 0.00032588 | 204 | 82920 | Planned | Planned
1391 |  | 35489 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-30 | 45503.375 | 2024-07-30 | 45503.6375 | 7.3484e-05 | 6.388e-06 | 4 | 46 | Planned | Planned
1392 |  | 35490 | HILL K09 - K09 3 MELROSE RD | Auckland | HILL K09 | 2024-07-30 | 45503.4201 | 2024-07-30 | 45503.559 | 0.014697 | 7.3483e-05 | 46 | 9200 | Planned | Planned
1393 |  | 35491 | FORR K11 - K11 BLAKEBOROUGH DR + LS | Northern | FORR K11 | 2024-07-30 | 45503.4486 | 2024-07-30 | 45503.9451 | 0.0091375 | 1.278e-05 | 8 | 5720 | Unplanned | Defective equipment
1394 |  | 35492 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-07-30 | 45503.5069 | 2024-07-30 | 45503.6722 | 0.02397 | 0.00061662 | 386 | 15005 | Unplanned | Vegetation
1395 |  | 35493 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-07-30 | 45503.4604 | 2024-07-30 | 45503.6646 | 0.024203 | 0.00017411 | 109 | 15151 | Unplanned | Defective equipment
1396 |  | 35494 | SNEL K08 - K08 ALGIES BAY | Northern | SNEL K08 | 2024-07-30 | 45503.6806 | 2024-07-30 | 45503.7069 | 0.0046742 | 0.00012301 | 77 | 2926 | Unplanned | Defective equipment
1397 |  | 35495 | WEST K09 - K09 TELSTRA SATURN | Auckland | WEST K09 | 2024-07-30 | 45503.6458 | 2024-07-30 | 45503.6806 | 7.9873e-05 | 1.597e-06 | 1 | 50 | Unplanned | Defective equipment
1398 |  | 35496 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2024-07-30 | 45503.7639 | 2024-07-30 | 45503.7778 | 0.0013738 | 6.8691e-05 | 43 | 860 | Unplanned | Defective equipment
1399 |  | 35497 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-07-30 | 45503.9646 | 2024-07-31 | 45504.0583 | 0.0071167 | 5.2715e-05 | 33 | 4455 | Unplanned | Wildlife
1400 |  | 35498 | REMU K19 - K19 ENTRICAN AVE 21 | Auckland | REMU K19 | 2024-07-31 | 45504.0903 | 2024-07-31 | 45504.275 | 0.016147 | 6.0703e-05 | 38 | 10108 | Unplanned | Third party interference
1401 |  | 35499 | GULF K05 - K05 ALEC CRAIG WAY | Northern | GULF K05 | 2024-07-31 | 45504.3333 | 2024-07-31 | 45504.6229 | 0.0066614 | 1.5973e-05 | 10 | 4170 | Planned | Planned
1402 |  | 35500 | BROW K02 - K02 OTEHA VALLEY ROAD | Northern | BROW K02 | 2024-07-31 | 45504.375 | 2024-07-31 | 45504.55 | 0.037438 | 0.00014856 | 93 | 23436 | Planned | Planned
1403 |  | 35501 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-07-31 | 45504.375 | 2024-07-31 | 45504.7083 | 0.12947 | 0.00027636 | 173 | 81045 | Planned | Planned
1404 |  | 35502 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-07-31 | 45504.3333 | 2024-07-31 | 45504.7306 | 0.18674 | 0.00033228 | 208 | 116896 | Planned | Planned
1405 |  | 35503 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-31 | 45504.375 | 2024-07-31 | 45504.5833 | 0.051758 | 0.00017252 | 108 | 32400 | Planned | Planned
1406 |  | 35504 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-07-31 | 45504.375 | 2024-07-31 | 45504.6368 | 0.0015224 | 0.00011981 | 75 | 953 | Planned | Planned
1407 |  | 35505 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-07-31 | 45504.9167 | 2024-08-01 | 45505.1958 | 0.10556 | 0.00033227 | 208 | 66083 | Planned | Planned
1408 |  | 35506 | NEWT K12 - K12 AIR NEW ZEALAND COMPUTER CENTRE | Auckland | NEWT K12 | 2024-07-31 | 45504.9792 | 2024-08-01 | 45505.0792 | 0.047847 | 0.00033227 | 208 | 29952 | Planned | Planned
1409 |  | 35507 | MANU K22 - K22 HOLMES RD | Auckland | MANU K22 | 2024-08-01 | 45505.0417 | 2024-08-01 | 45505.0896 | 0.0029761 | 4.3131e-05 | 27 | 1863 | Planned | Planned
1410 |  | 35508 | ORAT K02 - K02 PARKER ROAD | Northern | ORAT K02 | 2024-08-01 | 45505.3611 | 2024-08-01 | 45505.734 | 0.010294 | 1.917e-05 | 12 | 6444 | Planned | Planned
1411 |  | 35509 | SUNS K11 - K11 PARKWAY DRIVE | Northern | SUNS K11 | 2024-08-01 | 45505.9167 | 2024-08-02 | 45506.0847 | 0.0077317 | 3.1949e-05 | 20 | 4840 | Planned | Planned
1412 |  | 35510 | MANU K07 - K07 HALVER RD | Auckland | MANU K07 | 2024-08-01 | 45505.9792 | 2024-08-02 | 45506.1403 | 0.072748 | 0.00032109 | 201 | 45540 | Planned | Planned
1413 |  | 35511 | BMON K02 - K02 NARROW NECK | Northern | BMON K02 | 2024-08-02 | 45506.1924 | 2024-08-02 | 45506.2118 | 4.4729e-05 | 1.597e-06 | 1 | 28 | Planned | Planned
1414 |  | 35512 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2024-08-02 | 45506.3958 | 2024-08-02 | 45506.5917 | 0.12794 | 0.00045368 | 284 | 80088 | Planned | Planned
1415 |  | 35514 | GULF K15 - K15 EVERARD AVE + LS | Northern | GULF K08 | 2024-08-02 | 45506.3333 | 2024-08-02 | 45506.5243 | 0.064831 | 0.00028435 | 178 | 40584 | Planned | Planned
1416 |  | 35514 | GULF K15 - K15 EVERARD AVE + LS | Northern | GULF K15 | 2024-08-02 | 45506.3333 | 2024-08-02 | 45506.5243 | 0.08171 | 0.00029713 | 186 | 51150 | Planned | Planned
1417 |  | 35515 | BUSH K04 - K04 UNSWORTH DRIVE | Northern | BUSH K04 | 2024-08-02 | 45506.3549 | 2024-08-02 | 45506.4104 | 0.011078 | 0.00016454 | 103 | 6935 | Unplanned | Defective equipment
1418 |  | 35516 | QUAY K07 - K07 FORT STREET | Auckland | QUAY K07 | 2024-08-02 | 45506.3569 | 2024-08-07 | 45511.684 | 0.00036422 | 1.598e-06 | 1 | 228 | Unplanned | Defective equipment
1419 |  | 35516 | QUAY K07 - K07 FORT STREET | Auckland | QUAY K23 | 2024-08-02 | 45506.3569 | 2024-08-07 | 45511.684 | 0.10463 | 0.00048882 | 306 | 65500 | Unplanned | Defective equipment
1420 |  | 35517 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-02 | 45506.3958 | 2024-08-02 | 45506.7035 | 0.010615 | 2.3962e-05 | 15 | 6645 | Planned | Planned
1421 |  | 35518 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-08-02 | 45506.6215 | 2024-08-02 | 45506.6542 | 0.0022876 | 0.00017252 | 108 | 1432 | Planned | Planned
1422 |  | 35520 | HILL K01 - K01 2 HAUGHEY AVE | Auckland | HILL K01 | 2024-08-02 | 45506.9174 | 2024-08-03 | 45507.3521 | 0.38324 | 0.00078275 | 398 | 239904 | Planned | Planned
1423 |  | 35521 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2024-08-02 | 45506.9674 | 2024-08-03 | 45507.1687 | 0.18253 | 0.0006294 | 394 | 114260 | Planned | Planned
1424 |  | 35522 | CHEV K04 - K04 MOA RD | Auckland | CHEV K04 | 2024-08-03 | 45507.1667 | 2024-08-03 | 45507.2694 | 0.064071 | 0.00043291 | 271 | 40108 | Planned | Planned
1425 |  | 35524 | BROW K04 - K04 NORTHCROSS | Northern | BROW K04 | 2024-08-03 | 45507.3542 | 2024-08-03 | 45507.8278 | 0.046842 | 7.1887e-05 | 45 | 29323 | Planned | Planned
1426 |  | 35524 | BROW K04 - K04 NORTHCROSS | Northern | BROW K12 | 2024-08-03 | 45507.3542 | 2024-08-03 | 45507.8278 | 0.086068 | 0.0001262 | 79 | 53878 | Planned | Planned
1427 |  | 35525 | HBUR K04 - K04 AORANGI PLACE | Northern | HBUR K04 | 2024-08-03 | 45507.2979 | 2024-08-03 | 45507.6424 | 0.00037061 | 1.278e-05 | 4 | 232 | Planned | Planned
1428 |  | 35526 | BIRK K12 - K12 STANLEY ROAD | Northern | BIRK K12 | 2024-08-03 | 45507.3785 | 2024-08-03 | 45507.6778 | 0.024098 | 5.5911e-05 | 35 | 15085 | Planned | Planned
1429 |  | 35527 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-08-03 | 45507.6771 | 2024-08-03 | 45507.691 | 9.5848e-05 | 4.792e-06 | 3 | 60 | Unplanned | Other Cause | Outage caused by Tap Operation
1430 |  | 35528 | MEAS K13 - K13 BUCKLAND RD | Auckland | MEAS K13 | 2024-08-03 | 45507.7049 | 2024-08-03 | 45507.7667 | 0.00042652 | 4.791e-06 | 3 | 267 | Unplanned | Cause unknown
1431 |  | 35529 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-08-03 | 45507.6701 | 2024-08-03 | 45507.684 | 3.1949e-05 | 1.597e-06 | 1 | 20 | Planned | Planned
1432 |  | 35530 | CHEV K05 - K05 PT CHEVALIER RD 22 | Auckland | CHEV K05 | 2024-08-04 | 45508.316 | 2024-08-04 | 45508.5021 | 0.27767 | 0.001901 | 1190 | 173822 | Unplanned | Wildlife
1433 |  | 35531 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-08-04 | 45508.341 | 2024-08-04 | 45508.8417 | 0.0046071 | 6.39e-06 | 4 | 2884 | Unplanned | Defective equipment
1434 |  | 35532 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-08-04 | 45508.8819 | 2024-08-05 | 45509.2201 | 0.062283 | 0.0005 | 313 | 38989 | Unplanned | Vegetation
1435 |  | 35534 | SUNS K08 - K08 TARGET ROAD | Northern | JAME K04 | 2024-08-05 | 45509.3958 | 2024-08-05 | 45509.5861 | 0.035869 | 0.00017412 | 109 | 22454 | Planned | Planned
1436 |  | 35534 | SUNS K08 - K08 TARGET ROAD | Northern | SUNS K08 | 2024-08-05 | 45509.3958 | 2024-08-05 | 45509.5861 | 0.024074 | 8.7861e-05 | 55 | 15070 | Planned | Planned
1437 |  | 35535 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-08-05 | 45509.4187 | 2024-08-05 | 45509.5542 | 0.0028035 | 1.4377e-05 | 9 | 1755 | Planned | Planned
1438 |  | 35537 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-08-05 | 45509.3986 | 2024-08-12 | 45516.3396 | 0.015967 | 1.597e-06 | 1 | 9995 | Unplanned | Third party interference
1439 |  | 35538 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-08-05 | 45509.6368 | 2024-08-07 | 45511.9444 | 0.011091 | 0.002893 | 1811 | 6943 | Unplanned | Defective equipment
1440 |  | 35539 | BUSH K11 - K11 SCHNAPPER ROCK ROAD + LS | Northern | BUSH K11 | 2024-08-05 | 45509.616 | 2024-08-05 | 45509.6854 | 0.00015975 | 1.597e-06 | 1 | 100 | Unplanned | Cause unknown
1441 |  | 35540 | KING K12 - K12 GT NORTH RD | Auckland | KING K12 | 2024-08-05 | 45509.7993 | 2024-08-05 | 45509.9674 | 0.20483 | 0.0012892 | 807 | 128222 | Unplanned | Cause unknown
1442 |  | 35541 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-05 | 45509.7604 | 2024-08-05 | 45509.8681 | 0.00049521 | 3.195e-06 | 2 | 310 | Unplanned | Cause unknown
1443 |  | 35542 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-05 | 45509.9132 | 2024-08-06 | 45510.1056 | 0.021491 | 0.0016422 | 389 | 13453 | Unplanned | Third party interference
1444 |  | 35543 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-08-05 | 45509.7639 | 2024-08-05 | 45509.9854 | 0.00050959 | 1.597e-06 | 1 | 319 | Planned | Planned
1445 |  | 35544 | BRIC K10 - K10 ASTLEY AVE | Northern | BRIC K10 | 2024-08-06 | 45510.209 | 2024-08-07 | 45511.2326 | 0.22078 | 0.00080512 | 381 | 138204 | Planned | Planned
1446 |  | 35546 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-08-06 | 45510.3333 | 2024-08-06 | 45510.6917 | 0.00082429 | 1.597e-06 | 1 | 516 | Planned | Planned
1447 |  | 35547 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-08-06 | 45510.375 | 2024-08-06 | 45510.7118 | 0.036414 | 7.508e-05 | 47 | 22795 | Planned | Planned
1448 |  | 35548 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-08-06 | 45510.375 | 2024-08-06 | 45510.7153 | 0.078276 | 0.00015975 | 100 | 49000 | Planned | Planned
1449 |  | 35549 | NSBT48 - SWANSON H04 - SIMPSON RD P264 (48) | Northern | SIMP K07 | 2024-08-06 | 45510.3542 | 2024-08-06 | 45510.659 | 0.024735 | 7.8274e-05 | 49 | 15484 | Planned | Planned
1450 |  | 35550 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2024-08-07 | 45511.0424 | 2024-08-07 | 45511.1833 | 0.12809 | 0.000631 | 395 | 80185 | Planned | Planned
1451 |  | 35551 | SAND K13 - K13 2 MAYN AVE | Auckland | SAND K13 | 2024-08-06 | 45510.9174 | 2024-08-25 | 45529.1965 | 0.10954 | 0.00029553 | 185 | 68570 | Planned | Planned
1452 |  | 35552 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-08-07 | 45511.334 | 2024-08-07 | 45511.55 | 0.00049681 | 1.597e-06 | 1 | 311 | Planned | Planned
1453 |  | 35553 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-08-07 | 45511.3785 | 2024-08-07 | 45511.6389 | 0.045528 | 0.00012141 | 76 | 28500 | Planned | Planned
1454 |  | 35554 | OREW K10 - K10 HATFIELDS | Northern | OREW K10 | 2024-08-07 | 45511.3764 | 2024-08-07 | 45511.6229 | 0.091028 | 0.00027157 | 170 | 56983 | Planned | Planned
1455 |  | 35555 | SABU K07 - K07 AWAROA RD | Northern | SABU K07 | 2024-08-07 | 45511.3333 | 2024-08-07 | 45511.75 | 0.085304 | 0.00014217 | 89 | 53400 | Planned | Planned
1456 |  | 35556 | TRIA K02 - K02 SOUTH | Northern | TRIA K02 | 2024-08-07 | 45511.3542 | 2024-08-07 | 45511.6389 | 0.099554 | 0.00024281 | 152 | 62320 | Planned | Planned
1457 |  | 35557 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-08-07 | 45511.375 | 2024-08-07 | 45511.7361 | 0.079745 | 0.00015336 | 96 | 49920 | Planned | Planned
1458 |  | 35558 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-07 | 45511.3347 | 2024-08-07 | 45511.6396 | 0.032259 | 7.3478e-05 | 46 | 20194 | Planned | Planned
1459 |  | 35559 | HOBV K04 - K04 ELIZABETH DR | Northern | HOBV K04 | 2024-08-07 | 45511.4688 | 2024-08-07 | 45511.4778 | 0.020331 | 0.0015895 | 995 | 12727 | Unplanned | Cause unknown
1460 |  | 35560 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-08-07 | 45511.5208 | 2024-08-07 | 45511.7257 | 0.30586 | 0.0035336 | 2212 | 191469 | Unplanned | Cause unknown
1461 |  | 35561 | ORAK K01 - K01 KEMPTHORNE CRES | Auckland | ORAK K01 | 2024-08-07 | 45511.9792 | 2024-08-08 | 45512.1424 | 0.087093 | 0.00037061 | 232 | 54520 | Planned | Planned
1462 |  | 35562 | BIRK K12 - K12 STANLEY ROAD | Northern | BIRK K12 | 2024-08-07 | 45511.4951 | 2024-08-08 | 45512.1646 | 0.11396 | 0.00011821 | 74 | 71336 | Unplanned | Defective equipment
1463 |  | 35563 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-08-08 | 45512.3333 | 2024-08-08 | 45512.6076 | 0.11786 | 0.00029873 | 187 | 73781 | Planned | Planned
1464 |  | 35564 | TORB K07 - K07 GLAMORGAN DRIVE | Northern | TORB K07 | 2024-08-08 | 45512.3542 | 2024-08-08 | 45512.7444 | 0.096959 | 0.00017253 | 108 | 60696 | Planned | Planned
1465 |  | 35565 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-08-08 | 45512.375 | 2024-08-08 | 45512.7535 | 0.018283 | 3.3545e-05 | 21 | 11445 | Planned | Planned
1466 |  | 35566 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-08-08 | 45512.384 | 2024-08-08 | 45512.6917 | 0.066521 | 0.00015016 | 94 | 41642 | Planned | Planned
1467 |  | 35567 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-08-08 | 45512.6528 | 2024-08-08 | 45512.6729 | 0.0012508 | 4.313e-05 | 27 | 783 | Unplanned | Cause unknown
1468 |  | 35568 | QUAY J01 - J01 EAST ON QUAY AND RIPPLE NO.2 | Auckland | LIVE J04 | 2024-08-08 | 45512.6167 | 2024-08-08 | 45512.6208 | 0.0013227 | 0.00022045 | 138 | 828 | Unplanned | Human error
1469 |  | 35568 | QUAY J01 - J01 EAST ON QUAY AND RIPPLE NO.2 | Auckland | QUAY J01 | 2024-08-08 | 45512.6167 | 2024-08-08 | 45512.6208 | 1.917e-05 | 3.194e-06 | 2 | 12 | Unplanned | Human error
1470 |  | 35569 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-08-08 | 45512.9792 | 2024-08-09 | 45513.1528 | 0.082669 | 0.00033066 | 207 | 51750 | Planned | Planned
1471 |  | 35570 | BUSH K11 - K11 SCHNAPPER ROCK ROAD + LS | Northern | BUSH K11 | 2024-08-08 | 45512.875 | 2024-08-09 | 45513.0833 | 0.014856 | 4.9521e-05 | 31 | 9300 | Planned | Planned
1472 |  | 35571 | SABU K01 - K01 ST LEONARDS RD + LS | Northern | SABU K01 | 2024-08-09 | 45513.1201 | 2024-08-09 | 45513.5944 | 0.277 | 0.0038371 | 1201 | 173401 | Unplanned | Vegetation
1473 |  | 35572 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-08-09 | 45513.0451 | 2024-08-09 | 45513.1556 | 0.018288 | 0.00011501 | 72 | 11448 | Unplanned | Wildlife
1474 |  | 35573 | TATA K11 - K11 YEOVIL ROAD | Northern | TATA K11 | 2024-08-09 | 45513.3569 | 2024-08-09 | 45513.5354 | 0.02217 | 8.6263e-05 | 54 | 13878 | Planned | Planned
1475 |  | 35575 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-08-09 | 45513.3139 | 2024-08-09 | 45513.359 | 0.028671 | 0.00050002 | 313 | 17948 | Unplanned | Wildlife
1476 |  | 35576 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-08-09 | 45513.3021 | 2024-08-09 | 45513.3646 | 0.00028754 | 3.195e-06 | 2 | 180 | Unplanned | Wildlife
1477 |  | 35578 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-09 | 45513.4201 | 2024-08-09 | 45513.4271 | 1.5975e-05 | 1.597e-06 | 1 | 10 | Planned | Planned
1478 |  | 35579 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-08-09 | 45513.5028 | 2024-08-09 | 45513.6507 | 0.00034026 | 1.597e-06 | 1 | 213 | Planned | Planned
1479 |  | 35580 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-09 | 45513.3521 | 2024-08-09 | 45513.4375 | 0.00098244 | 7.987e-06 | 5 | 615 | Unplanned | Cause unknown
1480 |  | 35581 | ATKI K09 - K09 KAURILANDS RD | Northern | ATKI K09 | 2024-08-09 | 45513.5028 | 2024-08-09 | 45513.5694 | 0.0073611 | 7.6678e-05 | 48 | 4608 | Unplanned | Defective equipment
1481 |  | 35583 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-08-09 | 45513.6722 | 2024-08-09 | 45513.7319 | 0.00096167 | 1.1182e-05 | 7 | 602 | Unplanned | Defective equipment
1482 |  | 35584 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-08-10 | 45514 | 2024-08-10 | 45514.2347 | 0.20896 | 0.00061822 | 387 | 130806 | Planned | Planned
1483 |  | 35586 | WOOD K01 - K01 LINCOLN ROAD | Northern | WOOD K01 | 2024-08-10 | 45514.3757 | 2024-08-10 | 45514.6458 | 0.0012428 | 3.195e-06 | 2 | 778 | Planned | Planned
1484 |  | 35587 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-08-10 | 45514.5132 | 2024-08-10 | 45514.5431 | 0.01415 | 0.00032908 | 206 | 8858 | Unplanned | Defective equipment
1485 |  | 35588 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-08-10 | 45514.5785 | 2024-08-10 | 45514.7306 | 0.00034984 | 1.597e-06 | 1 | 219 | Unplanned | Other Cause | Outage on Non-Vector asset
1486 |  | 35589 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-08-10 | 45514.9167 | 2024-08-11 | 45515.1472 | 0.0010607 | 3.195e-06 | 2 | 664 | Planned | Planned
1487 |  | 35590 | TPAP K11 - K11 NZ RIBBON | Auckland | TPAP K11 | 2024-08-11 | 45515.316 | 2024-08-11 | 45515.6924 | 0.0043291 | 7.987e-06 | 5 | 2710 | Planned | Planned
1488 |  | 35591 | WAIM K03 - K03 REWITI | Northern | WAIM K03 | 2024-08-11 | 45515.3139 | 2024-08-11 | 45515.3785 | 0.0025256 | 2.7156e-05 | 17 | 1581 | Unplanned | Cause unknown
1489 |  | 35592 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-11 | 45515.3924 | 2024-08-11 | 45515.434 | 9.5848e-05 | 1.597e-06 | 1 | 60 | Unplanned | Wildlife
1490 |  | 35593 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-08-11 | 45515.6285 | 2024-08-11 | 45515.6993 | 0.00048882 | 4.792e-06 | 3 | 306 | Unplanned | Cause unknown
1491 |  | 35594 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-08-12 | 45516.0229 | 2024-08-12 | 45516.1083 | 0.04362 | 0.00035463 | 222 | 27306 | Unplanned | Cause unknown
1492 |  | 35596 | BROW K12 - K12 OKURA | Northern | BROW K12 | 2024-08-12 | 45516.3542 | 2024-08-12 | 45516.7222 | 0.061224 | 0.00015655 | 98 | 38326 | Planned | Planned
1493 |  | 35597 | ROCK K17 - K17 ORANGA AVE | Auckland | ROCK K17 | 2024-08-12 | 45516.375 | 2024-08-12 | 45516.7083 | 0.15588 | 0.00032748 | 205 | 97580 | Planned | Planned
1494 |  | 35598 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-08-12 | 45516.4271 | 2024-08-12 | 45516.6694 | 0.012823 | 3.6741e-05 | 23 | 8027 | Planned | Planned
1495 |  | 35599 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-08-12 | 45516.5722 | 2024-08-12 | 45516.8493 | 0.015791 | 0.00010064 | 63 | 9885 | Unplanned | Defective equipment
1496 |  | 35600 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-08-12 | 45516.6528 | 2024-08-12 | 45516.7188 | 0.0018211 | 1.9169e-05 | 12 | 1140 | Unplanned | Cause unknown
1497 |  | 35601 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-08-13 | 45517.1701 | 2024-08-13 | 45517.7396 | 0.014538 | 8.9463e-05 | 42 | 9101 | Planned | Planned
1498 |  | 35602 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | AVON K03 | 2024-08-12 | 45516.5535 | 2024-08-13 | 45517.0701 | 0.033821 | 0.00091375 | 572 | 21172 | Unplanned | Third party interference
1499 |  | 35603 | SHEL K08 - K08 MASKELL ST | Auckland | SHEL K08 | 2024-08-13 | 45517.3958 | 2024-08-13 | 45517.4757 | 0.00018371 | 1.597e-06 | 1 | 115 | Planned | Planned
1500 |  | 35604 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-08-13 | 45517.3979 | 2024-08-13 | 45517.7486 | 0.12907 | 0.00025559 | 160 | 80800 | Planned | Planned
1501 |  | 35605 | NLYN K04 - K04 RATA ST | Northern | NLYN K04 | 2024-08-13 | 45517.4194 | 2024-08-13 | 45517.5896 | 0.028571 | 0.00011661 | 73 | 17885 | Planned | Planned
1502 |  | 35606 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-08-13 | 45517.4465 | 2024-08-13 | 45517.5917 | 0.00033387 | 1.597e-06 | 1 | 209 | Planned | Planned
1503 |  | 35607 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-13 | 45517.7722 | 2024-08-13 | 45517.8611 | 0.0012268 | 9.584e-06 | 6 | 768 | Unplanned | Cause unknown
1504 |  | 35608 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-13 | 45517.9375 | 2024-08-14 | 45518.125 | 0.030623 | 0.00011342 | 71 | 19170 | Planned | Planned
1505 |  | 35609 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-08-13 | 45517.9076 | 2024-08-13 | 45517.9632 | 0.00076678 | 9.585e-06 | 6 | 480 | Unplanned | Defective equipment
1506 |  | 35610 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-08-13 | 45517.9875 | 2024-08-14 | 45518.0396 | 0.025395 | 0.0014329 | 897 | 15897 | Unplanned | Cause unknown
1507 |  | 35611 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-08-14 | 45518.2604 | 2024-08-14 | 45518.9403 | 0.018628 | 0.00034827 | 109 | 11661 | Unplanned | Human error
1508 |  | 35612 | NGAT K01 - K01 CALLIOPE ROAD | Northern | NGAT K01 | 2024-08-14 | 45518.3542 | 2024-08-14 | 45518.6972 | 0.19571 | 0.00039617 | 248 | 122512 | Planned | Planned
1509 |  | 35614 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-08-14 | 45518.375 | 2024-08-14 | 45518.6813 | 0.046496 | 0.00010543 | 66 | 29106 | Planned | Planned
1510 |  | 35615 | BALM K04 - K04 TRURO ROAD | Auckland | BALM K04 | 2024-08-14 | 45518.4361 | 2024-08-14 | 45518.809 | 0.082352 | 0.00015336 | 96 | 51552 | Planned | Planned
1511 |  | 35616 | MNAB K33 - K33 GAVIN STREET EAST | Auckland | MNAB K33 | 2024-08-14 | 45518.6674 | 2024-08-14 | 45518.7757 | 0.037131 | 0.00023802 | 149 | 23244 | Planned | Planned
1512 |  | 35617 | NGAT K01 - K01 CALLIOPE ROAD | Northern | NGAT K01 | 2024-08-14 | 45518.8757 | 2024-08-15 | 45519.0403 | 0.032559 | 0.00013738 | 86 | 20382 | Planned | Planned
1513 |  | 35619 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-08-15 | 45519.3125 | 2024-08-15 | 45519.7285 | 0.0076039 | 1.2779e-05 | 8 | 4760 | Planned | Planned
1514 |  | 35620 | HBUR K04 - K04 AORANGI PLACE | Northern | HBUR K04 | 2024-08-15 | 45519.3333 | 2024-08-15 | 45519.7 | 0.086876 | 0.00016454 | 103 | 54384 | Planned | Planned
1515 |  | 35621 | BIRK K11 - K11 BEACH HAVEN | Northern | BIRK K11 | 2024-08-15 | 45519.3333 | 2024-08-15 | 45519.6806 | 0.027956 | 5.5911e-05 | 35 | 17500 | Planned | Planned
1516 |  | 35622 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-08-15 | 45519.4194 | 2024-08-15 | 45519.5521 | 0.010984 | 5.7509e-05 | 36 | 6876 | Unplanned | Defective equipment
1517 |  | 35623 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-08-15 | 45519.4132 | 2024-08-15 | 45519.6771 | 0.011534 | 3.0352e-05 | 19 | 7220 | Planned | Planned
1518 |  | 35624 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-08-15 | 45519.4021 | 2024-08-15 | 45519.6764 | 0.001893 | 4.792e-06 | 3 | 1185 | Planned | Planned
1519 |  | 35625 | HOBS J34 - J34 QUAY WEST | Auckland | HOBS J34 | 2024-08-15 | 45519.2639 | 2024-08-15 | 45519.4236 | 0.01139 | 4.9521e-05 | 31 | 7130 | Unplanned | Third party interference
1520 |  | 35626 | RANU K08 - K08 MIHINI ROAD | Northern | RANU K08 | 2024-08-15 | 45519.875 | 2024-08-15 | 45519.9924 | 0.00053994 | 3.195e-06 | 2 | 338 | Planned | Planned
1521 |  | 35627 | JAME K01 - K01 WELDENE | Northern | JAME K01 | 2024-08-15 | 45519.9347 | 2024-08-16 | 45520.0104 | 0.0078355 | 7.1885e-05 | 45 | 4905 | Unplanned | Defective equipment
1522 |  | 35628 | NEWM K12 - K12 SUITER ST LION BUILDING | Auckland | NEWM K12 | 2024-08-16 | 45520 | 2024-08-16 | 45520.2125 | 0.00048882 | 1.597e-06 | 1 | 306 | Planned | Planned
1523 |  | 35629 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-16 | 45520.3549 | 2024-08-16 | 45520.5903 | 0.017871 | 5.2714e-05 | 33 | 11187 | Planned | Planned
1524 |  | 35630 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-16 | 45520.3875 | 2024-08-16 | 45520.4646 | 0.010994 | 9.9036e-05 | 62 | 6882 | Planned | Planned
1525 |  | 35631 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-08-16 | 45520.3764 | 2024-08-16 | 45520.4806 | 0.0033547 | 2.2365e-05 | 14 | 2100 | Planned | Planned
1526 |  | 35632 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2024-08-16 | 45520.375 | 2024-08-16 | 45520.6757 | 0.043577 | 0.00010064 | 63 | 27279 | Planned | Planned
1527 |  | 35633 | SHOW K05 - K05 LITTEN RD | Auckland | SHOW K05 | 2024-08-16 | 45520.2792 | 2024-08-16 | 45520.5417 | 0.055802 | 0.00035623 | 223 | 34932 | Unplanned | Cause unknown
1528 |  | 35634 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-16 | 45520.4201 | 2024-08-16 | 45520.6319 | 0.0024361 | 7.987e-06 | 5 | 1525 | Planned | Planned
1529 |  | 35635 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-08-16 | 45520.4701 | 2024-08-16 | 45520.5903 | 0.002893 | 7.6676e-05 | 48 | 1811 | Planned | Planned
1530 |  | 35636 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-16 | 45520.5354 | 2024-08-16 | 45520.9875 | 0.10258 | 0.00088667 | 405 | 64215 | Unplanned | Third party interference
1531 |  | 35637 | BROW K12 - K12 OKURA | Northern | BROW K12 | 2024-08-16 | 45520.5958 | 2024-08-16 | 45520.6125 | 0.0010352 | 4.3131e-05 | 27 | 648 | Planned | Planned
1532 |  | 35638 | HOWI K10 - K10 FINNERTY AVE | Auckland | HOWI K10 | 2024-08-17 | 45521.0778 | 2024-08-17 | 45521.1396 | 0.18255 | 0.0020511 | 1284 | 114276 | Unplanned | Defective equipment
1533 |  | 35639 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-08-17 | 45521.375 | 2024-08-17 | 45521.684 | 0.073659 | 0.00016933 | 106 | 46110 | Planned | Planned
1534 |  | 35640 | SABU K08 - K08 GREAT NORTH RD | Northern | SABU K08 | 2024-08-17 | 45521.3785 | 2024-08-17 | 45521.75 | 0.065807 | 0.000123 | 77 | 41195 | Planned | Planned
1535 |  | 35642 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-08-17 | 45521.625 | 2024-08-17 | 45521.8771 | 0.11504 | 0.0006294 | 394 | 72013 | Unplanned | Vegetation
1536 |  | 35643 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-08-17 | 45521.6146 | 2024-08-17 | 45521.8451 | 0.0058339 | 1.7572e-05 | 11 | 3652 | Unplanned | Defective equipment
1537 |  | 35645 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-08-17 | 45521.925 | 2024-08-18 | 45522.009 | 0.019716 | 0.00016294 | 102 | 12342 | Unplanned | Defective equipment
1538 |  | 35646 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-18 | 45522.075 | 2024-08-18 | 45522.1813 | 0.038861 | 0.00025398 | 159 | 24327 | Unplanned | Vegetation
1539 |  | 35647 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2024-08-18 | 45522.1507 | 2024-08-18 | 45522.2049 | 0.067908 | 0.00087062 | 545 | 42510 | Unplanned | Vegetation
1540 |  | 35649 | ROSE K06 - K06 COPSEY PL | Auckland | ROSE K06 | 2024-08-18 | 45522.3354 | 2024-08-18 | 45522.6535 | 0.00073164 | 1.597e-06 | 1 | 458 | Planned | Planned
1541 |  | 35650 | MANL K05 - K05 ARKLES BAY | Northern | MANL K05 | 2024-08-18 | 45522.1632 | 2024-08-18 | 45522.3201 | 0.011553 | 5.1119e-05 | 32 | 7232 | Unplanned | Vegetation
1542 |  | 35651 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-08-18 | 45522.3083 | 2024-08-18 | 45522.384 | 0.054501 | 0.0005 | 313 | 34117 | Unplanned | Vegetation
1543 |  | 35653 | ATKI K08 - K08 DAFFODIL ST + LS | Northern | ATKI K08 | 2024-08-18 | 45522.325 | 2024-08-18 | 45522.3694 | 0.042016 | 0.00095209 | 596 | 26302 | Unplanned | Cause unknown
1544 |  | 35655 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-08-18 | 45522.3854 | 2024-08-18 | 45522.4201 | 0.00063898 | 1.278e-05 | 8 | 400 | Unplanned | Cause unknown
1545 |  | 35656 | LAIN K07 - K07 VICTORY RD | Northern | LAIN K07 | 2024-08-18 | 45522.4576 | 2024-08-18 | 45522.5944 | 0.084876 | 0.00048883 | 306 | 53132 | Unplanned | Vegetation
1546 |  | 35658 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-08-18 | 45522.4694 | 2024-08-18 | 45522.6667 | 0.082419 | 0.00068691 | 430 | 51594 | Unplanned | Cause unknown
1547 |  | 35659 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-08-18 | 45522.5222 | 2024-08-18 | 45522.6083 | 0.074154 | 0.00085465 | 535 | 46420 | Unplanned | Cause unknown
1548 |  | 35659 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K05 | 2024-08-18 | 45522.5222 | 2024-08-18 | 45522.6083 | 7.6678e-05 | 1.917e-05 | 12 | 48 | Unplanned | Cause unknown
1549 |  | 35660 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-08-18 | 45522.5132 | 2024-08-18 | 45522.6653 | 0.065756 | 0.00073323 | 459 | 41163 | Unplanned | Vegetation
1550 |  | 35661 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-18 | 45522.5528 | 2024-08-18 | 45522.6285 | 0.0081838 | 7.5079e-05 | 47 | 5123 | Unplanned | Defective equipment
1551 |  | 35664 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-08-18 | 45522.5174 | 2024-08-18 | 45522.6771 | 0.041151 | 0.00017892 | 112 | 25760 | Unplanned | Cause unknown
1552 |  | 35665 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-08-18 | 45522.6264 | 2024-08-18 | 45522.6979 | 0.00016454 | 1.597e-06 | 1 | 103 | Unplanned | Vegetation
1553 |  | 35666 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-08-18 | 45522.3146 | 2024-08-18 | 45522.8264 | 0.0058866 | 7.987e-06 | 5 | 3685 | Unplanned | Cause unknown
1554 |  | 35667 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2024-08-18 | 45522.8236 | 2024-08-18 | 45522.9028 | 0.069748 | 0.00061183 | 383 | 43662 | Unplanned | Defective equipment
1555 |  | 35668 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-08-16 | 45520.334 | 2024-08-16 | 45520.425 | 0.00020927 | 1.597e-06 | 1 | 131 | Unplanned | Wildlife
1556 |  | 35669 | BUSH K04 - K04 UNSWORTH DRIVE | Northern | BUSH K04 | 2024-08-18 | 45522.834 | 2024-08-18 | 45522.8632 | 0.0010495 | 2.5559e-05 | 16 | 657 | Planned | Planned
1557 |  | 35670 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-08-18 | 45522.8757 | 2024-08-19 | 45523.2667 | 0.025269 | 4.9522e-05 | 31 | 15818 | Planned | Planned
1558 |  | 35671 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-08-19 | 45523.0472 | 2024-08-19 | 45523.0938 | 0.042384 | 0.0006326 | 396 | 26532 | Unplanned | Vegetation
1559 |  | 35672 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-19 | 45523.0687 | 2024-08-19 | 45523.1687 | 0.010812 | 7.5079e-05 | 47 | 6768 | Unplanned | Cause unknown
1560 |  | 35674 | ECOA K04 - K04 KNIGHTS ROAD | Northern | ECOA K04 | 2024-08-19 | 45523.0813 | 2024-08-19 | 45523.1542 | 0.21487 | 0.0020463 | 1281 | 134505 | Unplanned | Cause unknown
1561 |  | 35675 | ECOA K08 - K08 LYONS AVENUE | Northern | ECOA K08 | 2024-08-19 | 45523.0813 | 2024-08-19 | 45523.1549 | 0.12818 | 0.0012093 | 757 | 80242 | Unplanned | Cause unknown
1562 |  | 35676 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-08-19 | 45523.0861 | 2024-08-19 | 45523.1514 | 0.030403 | 0.00039458 | 247 | 19032 | Unplanned | Cause unknown
1563 |  | 35677 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-08-19 | 45523.1021 | 2024-08-19 | 45523.1708 | 0.029732 | 0.00030032 | 188 | 18612 | Unplanned | Cause unknown
1564 |  | 35678 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-08-19 | 45523.1257 | 2024-08-19 | 45523.2847 | 0.11513 | 0.00068691 | 430 | 72072 | Unplanned | Vegetation
1565 |  | 35679 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-08-19 | 45523.1674 | 2024-08-19 | 45523.3958 | 0.070649 | 0.00051761 | 162 | 44226 | Unplanned | Vegetation
1566 |  | 35681 | LAIN K07 - K07 VICTORY RD | Northern | LAIN K07 | 2024-08-19 | 45523.3111 | 2024-08-19 | 45523.4535 | 0.10021 | 0.00048882 | 306 | 62730 | Unplanned | Vegetation
1567 |  | 35682 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-08-19 | 45523.0632 | 2024-08-19 | 45523.3125 | 0.025807 | 7.1886e-05 | 45 | 16155 | Unplanned | Vegetation
1568 |  | 35683 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-08-19 | 45523.0736 | 2024-08-19 | 45523.3333 | 0.066914 | 0.00017892 | 112 | 41888 | Unplanned | Cause unknown
1569 |  | 35684 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-08-19 | 45523.3562 | 2024-08-19 | 45523.5569 | 0.019376 | 0.00016773 | 105 | 12129 | Unplanned | Vegetation
1570 |  | 35685 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-08-19 | 45523.0715 | 2024-08-19 | 45523.3542 | 0.0032508 | 7.987e-06 | 5 | 2035 | Unplanned | Cause unknown
1571 |  | 35686 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-08-19 | 45523.1403 | 2024-08-19 | 45523.3764 | 0.0065176 | 1.9169e-05 | 12 | 4080 | Unplanned | Cause unknown
1572 |  | 35687 | RANU K02 - K02 ZITA MARIA | Northern | RANU K02 | 2024-08-19 | 45523.3958 | 2024-08-19 | 45523.5583 | 0.014952 | 6.3898e-05 | 40 | 9360 | Planned | Planned
1573 |  | 35688 | ATKI K09 - K09 KAURILANDS RD | Northern | ATKI K09 | 2024-08-19 | 45523.4396 | 2024-08-19 | 45523.6694 | 0.28543 | 0.0013499 | 845 | 178679 | Unplanned | Defective equipment
1574 |  | 35689 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-19 | 45523.4424 | 2024-08-19 | 45523.6632 | 0.016401 | 0.00015177 | 58 | 10267 | Unplanned | Cause unknown
1575 |  | 35690 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-08-19 | 45523.35 | 2024-08-19 | 45523.4646 | 0.038746 | 0.00023483 | 147 | 24255 | Unplanned | Vegetation
1576 |  | 35692 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-08-19 | 45523.4271 | 2024-08-19 | 45523.5229 | 0.0030863 | 2.2364e-05 | 14 | 1932 | Unplanned | Defective equipment
1577 |  | 35693 | MEAS K13 - K13 BUCKLAND RD | Auckland | MEAS K13 | 2024-08-19 | 45523.441 | 2024-08-19 | 45523.6507 | 0.0014473 | 4.791e-06 | 3 | 906 | Unplanned | Defective equipment
1578 |  | 35694 | HBUR K11 - K11 HAMMOND PL | Northern | HBUR K11 | 2024-08-19 | 45523.5597 | 2024-08-19 | 45523.6174 | 0.075876 | 0.0017428 | 1091 | 47498 | Unplanned | Defective equipment
1579 |  | 35695 | LAIN K07 - K07 VICTORY RD | Northern | LAIN K07 | 2024-08-19 | 45523.5604 | 2024-08-19 | 45523.6889 | 0.090432 | 0.00048882 | 306 | 56610 | Unplanned | Cause unknown
1580 |  | 35696 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2024-08-19 | 45523.3778 | 2024-08-19 | 45523.6076 | 0.01269 | 3.8339e-05 | 24 | 7944 | Unplanned | Vegetation
1581 |  | 35699 | WEST K18 - K18 MT RICHMOND No.2 | Auckland | WEST K18 | 2024-08-19 | 45523.5903 | 2024-08-19 | 45523.7201 | 0.00029873 | 1.597e-06 | 1 | 187 | Unplanned | Defective equipment
1582 |  | 35701 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2024-08-19 | 45523.6729 | 2024-08-19 | 45523.7847 | 0.035235 | 0.00021884 | 137 | 22057 | Unplanned | Cause unknown
1583 |  | 35702 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-08-19 | 45523.4875 | 2024-08-20 | 45524.5062 | 0.016074 | 4.3131e-05 | 12 | 10062 | Unplanned | Defective equipment
1584 |  | 35703 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-08-19 | 45523.5986 | 2024-08-20 | 45524.6597 | 0.0024409 | 1.597e-06 | 1 | 1528 | Unplanned | Vegetation
1585 |  | 35704 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-08-19 | 45523.6333 | 2024-08-19 | 45523.7 | 0.0092014 | 9.5848e-05 | 60 | 5760 | Unplanned | Cause unknown
1586 |  | 35705 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-08-19 | 45523.609 | 2024-08-19 | 45523.7472 | 0.0047684 | 2.3962e-05 | 15 | 2985 | Unplanned | Cause unknown
1587 |  | 35706 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-08-19 | 45523.6743 | 2024-08-19 | 45523.9521 | 0.018197 | 0.00018689 | 117 | 11391 | Unplanned | Vegetation
1588 |  | 35707 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-08-19 | 45523.7431 | 2024-08-19 | 45523.7819 | 0.0044729 | 7.9873e-05 | 50 | 2800 | Unplanned | Defective equipment
1589 |  | 35708 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-08-19 | 45523.7861 | 2024-08-20 | 45524.0014 | 0.057317 | 0.00033068 | 207 | 35880 | Unplanned | Vegetation
1590 |  | 35709 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-08-19 | 45523.6806 | 2024-08-19 | 45523.809 | 0.0041374 | 2.2364e-05 | 14 | 2590 | Unplanned | Cause unknown
1591 |  | 35711 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2024-08-19 | 45523.8181 | 2024-08-19 | 45523.9472 | 0.14916 | 0.00080192 | 502 | 93372 | Unplanned | Defective equipment
1592 |  | 35712 | MKAU K27 - K27 CARTER HOLT (VIA LST1) | Auckland | MKAU K27 | 2024-08-19 | 45523.9167 | 2024-08-20 | 45524.159 | 0.16056 | 0.00046007 | 288 | 100512 | Planned | Planned
1593 |  | 35713 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-08-19 | 45523.8611 | 2024-08-20 | 45524.0764 | 0.004933 | 4.1534e-05 | 26 | 3088 | Unplanned | Defective equipment
1594 |  | 35714 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-08-20 | 45524.0076 | 2024-08-20 | 45524.2257 | 0.005016 | 1.5975e-05 | 10 | 3140 | Unplanned | Defective equipment
1595 |  | 35715 | MNAB K31 - K31 OLIVE RD | Auckland | MNAB K31 | 2024-08-20 | 45524.3361 | 2024-08-20 | 45524.3938 | 0.0033147 | 3.9936e-05 | 25 | 2075 | Unplanned | Defective equipment
1596 |  | 35716 | WEST K18 - K18 MT RICHMOND No.2 | Auckland | WEST K18 | 2024-08-20 | 45524.3333 | 2024-08-20 | 45524.4236 | 0.0010383 | 7.987e-06 | 5 | 650 | Planned | Planned
1597 |  | 35717 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-19 | 45523.75 | 2024-08-20 | 45524.434 | 0.012588 | 1.2779e-05 | 8 | 7880 | Unplanned | Cause unknown
1598 |  | 35718 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-20 | 45524.3771 | 2024-08-20 | 45524.6319 | 0.0029313 | 7.987e-06 | 5 | 1835 | Planned | Planned
1599 |  | 35719 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-08-20 | 45524.3993 | 2024-08-20 | 45524.5556 | 0.010783 | 4.7924e-05 | 30 | 6750 | Planned | Planned
1600 |  | 35720 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2024-08-20 | 45524.4271 | 2024-08-20 | 45524.6937 | 0.11568 | 0.0003163 | 198 | 72414 | Planned | Planned
1601 |  | 35721 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-08-20 | 45524.4264 | 2024-08-20 | 45524.7674 | 0.020102 | 4.9525e-05 | 31 | 12584 | Unplanned | Defective equipment
1602 |  | 35722 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-08-20 | 45524.7972 | 2024-08-20 | 45524.9792 | 0.0012556 | 4.792e-06 | 3 | 786 | Unplanned | Third party interference
1603 |  | 35723 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-08-20 | 45524.8979 | 2024-08-21 | 45525.2174 | 0.049234 | 0.00010703 | 67 | 30820 | Planned | Planned
1604 |  | 35724 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-20 | 45524.8688 | 2024-08-20 | 45524.941 | 0.0014952 | 1.4377e-05 | 9 | 936 | Unplanned | Cause unknown
1605 |  | 35725 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-08-20 | 45524.9625 | 2024-08-21 | 45525.0417 | 0.039518 | 0.00034665 | 217 | 24738 | Planned | Planned
1606 |  | 35727 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-08-20 | 45524.9958 | 2024-08-21 | 45525.0486 | 0.00012141 | 1.597e-06 | 1 | 76 | Unplanned | Third party interference
1607 |  | 35728 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-21 | 45525.1514 | 2024-08-21 | 45525.5938 | 0.17858 | 0.0037508 | 1225 | 111791 | Unplanned | Defective equipment
1608 |  | 35729 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2024-08-21 | 45525.2292 | 2024-08-21 | 45525.3167 | 0.0016102 | 1.2779e-05 | 8 | 1008 | Unplanned | Wildlife
1609 |  | 35730 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-08-21 | 45525.3333 | 2024-08-21 | 45525.5819 | 0.0028595 | 7.987e-06 | 5 | 1790 | Planned | Planned
1610 |  | 35731 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-08-21 | 45525.3403 | 2024-08-21 | 45525.8313 | 0.0033882 | 4.792e-06 | 3 | 2121 | Planned | Planned
1611 |  | 35732 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-08-21 | 45525.3562 | 2024-08-21 | 45525.7139 | 0.0041135 | 7.987e-06 | 5 | 2575 | Planned | Planned
1612 |  | 35733 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-08-21 | 45525.4382 | 2024-08-21 | 45525.4437 | 0.0025943 | 0.00032428 | 203 | 1624 | Planned | Planned
1613 |  | 35734 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-08-21 | 45525.4167 | 2024-08-21 | 45525.425 | 0.0018786 | 0.00015655 | 98 | 1176 | Planned | Planned
1614 |  | 35735 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-08-21 | 45525.375 | 2024-08-21 | 45525.7194 | 0.17748 | 0.00035783 | 224 | 111104 | Planned | Planned
1615 |  | 35736 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-08-21 | 45525.4861 | 2024-08-21 | 45525.7021 | 0.0019872 | 6.39e-06 | 4 | 1244 | Unplanned | Defective equipment
1616 |  | 35737 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-08-21 | 45525.8125 | 2024-08-21 | 45525.8285 | 7.3483e-05 | 3.195e-06 | 2 | 46 | Unplanned | Defective equipment
1617 |  | 35738 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-08-21 | 45525.9194 | 2024-08-21 | 45525.9736 | 0.02157 | 0.00064533 | 404 | 13503 | Unplanned | Cause unknown
1618 |  | 35740 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-08-22 | 45526.1875 | 2024-08-22 | 45526.2049 | 0.017995 | 0.00089618 | 561 | 11265 | Planned | Planned
1619 |  | 35741 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-08-22 | 45526.1875 | 2024-08-22 | 45526.2597 | 0.041202 | 0.00039617 | 248 | 25792 | Unplanned | Defective equipment
1620 |  | 35742 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-08-22 | 45526.375 | 2024-08-22 | 45526.716 | 0.011765 | 2.3962e-05 | 15 | 7365 | Planned | Planned
1621 |  | 35743 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-22 | 45526.4174 | 2024-08-22 | 45526.6389 | 0.0025479 | 7.987e-06 | 5 | 1595 | Planned | Planned
1622 |  | 35744 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-08-22 | 45526.4201 | 2024-08-22 | 45526.5833 | 0.00075081 | 3.195e-06 | 2 | 470 | Planned | Planned
1623 |  | 35745 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-22 | 45526.4271 | 2024-08-22 | 45526.441 | 3.1949e-05 | 1.597e-06 | 1 | 20 | Planned | Planned
1624 |  | 35746 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-08-22 | 45526.3819 | 2024-08-22 | 45526.5965 | 0.00049361 | 1.597e-06 | 1 | 309 | Unplanned | Cause unknown
1625 |  | 35747 | NEWT K09 - K09 A.R.A. WATERWORKS | Auckland | NEWT K09 | 2024-08-22 | 45526.6403 | 2024-08-22 | 45526.9049 | 0.0069202 | 6.0703e-05 | 38 | 4332 | Unplanned | Defective equipment
1626 |  | 35748 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-08-22 | 45526.7764 | 2024-08-22 | 45526.9667 | 0.045959 | 0.00016772 | 105 | 28770 | Unplanned | Defective equipment
1627 |  | 35749 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-08-22 | 45526.7778 | 2024-08-22 | 45526.8375 | 0.0012364 | 1.4376e-05 | 9 | 774 | Unplanned | Cause unknown
1628 |  | 35750 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-08-22 | 45526.9375 | 2024-08-23 | 45527.0931 | 0.052959 | 0.00023642 | 148 | 33152 | Planned | Planned
1629 |  | 35751 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-08-23 | 45527.0674 | 2024-08-23 | 45527.116 | 0.15711 | 0.0038115 | 2386 | 98347 | Unplanned | Third party interference
1630 |  | 35753 | OTAR K15 - K15 NZ WINES & SPIRITS | Auckland | OTAR K15 | 2024-08-23 | 45527.3125 | 2024-08-23 | 45527.4118 | 0.00045687 | 3.195e-06 | 2 | 286 | Planned | Planned
1631 |  | 35754 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-08-23 | 45527.1778 | 2024-08-23 | 45527.375 | 0.00045368 | 1.597e-06 | 1 | 284 | Unplanned | Wildlife
1632 |  | 35755 | TORB K08 - K08 GLENVAR ROAD | Northern | TORB K08 | 2024-08-23 | 45527.3333 | 2024-08-23 | 45527.7243 | 0.094044 | 0.00016933 | 106 | 58871 | Planned | Planned
1633 |  | 35756 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-23 | 45527.4194 | 2024-08-23 | 45527.6486 | 0.18925 | 0.00057348 | 359 | 118470 | Planned | Planned
1634 |  | 35757 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-08-23 | 45527.4938 | 2024-08-23 | 45527.7708 | 0.056727 | 0.00014217 | 89 | 35511 | Unplanned | Third party interference
1635 |  | 35758 | BAIR K04 - K04 ASHTON AVENUE | Auckland | BAIR K04 | 2024-08-23 | 45527.6535 | 2024-08-23 | 45527.684 | 0.036978 | 0.0023051 | 1443 | 23148 | Unplanned | Third party interference
1636 |  | 35758 | BAIR K04 - K04 ASHTON AVENUE | Auckland | MKAU K27 | 2024-08-23 | 45527.6535 | 2024-08-23 | 45527.684 | 0.083573 | 0.0018994 | 1189 | 52316 | Unplanned | Third party interference
1637 |  | 35759 | AVON K02 - K02 ST JUDE ST.(PENSIONER FLATS) | Auckland | AVON K02 | 2024-08-24 | 45528.0021 | 2024-08-24 | 45528.2771 | 0.20306 | 0.00051278 | 321 | 127116 | Planned | Planned
1638 |  | 35761 | ROSE K06 - K06 COPSEY PL | Auckland | ROSE K06 | 2024-08-24 | 45528.2292 | 2024-08-24 | 45528.5625 | 0.0015336 | 3.195e-06 | 2 | 960 | Unplanned | Defective equipment
1639 |  | 35762 | PAPA K10 - K10 17 PORCHESTER RD | Auckland | PAPA K10 | 2024-08-24 | 45528.4118 | 2024-08-24 | 45528.7562 | 0.00079234 | 1.597e-06 | 1 | 496 | Planned | Planned
1640 |  | 35763 | HOWI K09 - K09 HUTCHINSON RD | Auckland | HOWI K09 | 2024-08-24 | 45528.4257 | 2024-08-24 | 45528.5729 | 0.01761 | 8.3068e-05 | 52 | 11024 | Unplanned | Defective equipment
1641 |  | 35764 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2024-08-24 | 45528.4201 | 2024-08-24 | 45528.6167 | 0.22694 | 0.00080192 | 502 | 142066 | Planned | Planned
1642 |  | 35765 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-08-24 | 45528.3187 | 2024-08-24 | 45528.375 | 0.00090576 | 1.1182e-05 | 7 | 567 | Unplanned | Wildlife
1643 |  | 35766 | HOBS - Hobson | Auckland | HOBS K24 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.028984 | 0.00060383 | 189 | 18144 | Unplanned | Defective equipment
1644 |  | 35766 | HOBS - Hobson | Auckland | HOBS K25 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.0062301 | 0.0001917 | 60 | 3900 | Unplanned | Defective equipment
1645 |  | 35766 | HOBS - Hobson | Auckland | HOBS K26 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.0097765 | 0.00028754 | 90 | 6120 | Unplanned | Defective equipment
1646 |  | 35766 | HOBS - Hobson | Auckland | HOBS K27 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.028989 | 0.00084026 | 263 | 18147 | Unplanned | Defective equipment
1647 |  | 35766 | HOBS - Hobson | Auckland | HOBS K30 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.013866 | 0.00039617 | 124 | 8680 | Unplanned | Defective equipment
1648 |  | 35766 | HOBS - Hobson | Auckland | HOBS K32 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.036291 | 0.00098084 | 307 | 22718 | Unplanned | Defective equipment
1649 |  | 35766 | HOBS - Hobson | Auckland | HOBS K34 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.092378 | 0.0011694 | 732 | 57828 | Unplanned | Defective equipment
1650 |  | 35766 | HOBS - Hobson | Auckland | HOBS K35 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.081662 | 0.0010208 | 639 | 51120 | Unplanned | Defective equipment
1651 |  | 35766 | HOBS - Hobson | Auckland | HOBS K36 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.0028115 | 3.5134e-05 | 22 | 1760 | Unplanned | Defective equipment
1652 |  | 35766 | HOBS - Hobson | Auckland | HOBS K37 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.00012779 | 1.595e-06 | 1 | 80 | Unplanned | Defective equipment
1653 |  | 35766 | HOBS - Hobson | Auckland | HOBS K38 | 2024-08-24 | 45528.7146 | 2024-08-24 | 45528.7896 | 0.018403 | 0.00023003 | 144 | 11520 | Unplanned | Defective equipment
1654 |  | 35767 | WEST K16 - K16 SYLVIA PARK RD | Auckland | WEST K16 | 2024-08-25 | 45529.9583 | 2024-08-26 | 45530.0299 | 0.0013163 | 1.278e-05 | 8 | 824 | Planned | Planned
1655 |  | 35768 | SJOH K09 - K09 168 NORMAN LESSER DR | Auckland | SJOH K09 | 2024-08-26 | 45530.0833 | 2024-08-26 | 45530.175 | 0.012863 | 9.7445e-05 | 61 | 8052 | Planned | Planned
1656 |  | 35770 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-08-26 | 45530.375 | 2024-08-26 | 45530.5938 | 0.007548 | 2.3962e-05 | 15 | 4725 | Planned | Planned
1657 |  | 35771 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-08-26 | 45530.3875 | 2024-08-26 | 45530.625 | 0.01038 | 3.0351e-05 | 19 | 6498 | Planned | Planned
1658 |  | 35772 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-26 | 45530.3889 | 2024-08-26 | 45530.3958 | 1.5975e-05 | 1.597e-06 | 1 | 10 | Planned | Planned
1659 |  | 35773 | MNAB K03 - K03 LEONARD RD | Auckland | MNAB K03 | 2024-08-26 | 45530.6535 | 2024-08-27 | 45531.3333 | 0.0031278 | 3.195e-06 | 2 | 1958 | Unplanned | Defective equipment
1660 |  | 35774 | SAND K13 - K13 2 MAYN AVE | Auckland | SAND K13 | 2024-08-26 | 45530.9187 | 2024-08-27 | 45531.1813 | 0.10926 | 0.00028914 | 181 | 68396 | Planned | Planned
1661 |  | 35775 | WIRI K10 - K10 WIRI STATION RD WEST | Auckland | WIRI K10 | 2024-08-26 | 45530.9583 | 2024-08-27 | 45531.0528 | 0.0021725 | 1.5974e-05 | 10 | 1360 | Planned | Planned
1662 |  | 35776 | CLEN K07 - K07 ROBERT ROSS | Auckland | CLEN K07 | 2024-08-27 | 45531.0833 | 2024-08-27 | 45531.1528 | 0.00015975 | 1.597e-06 | 1 | 100 | Planned | Planned
1663 |  | 35777 | MWEL K01 - K01 MALONE RD | Auckland | MWEL K01 | 2024-08-27 | 45531.1715 | 2024-08-27 | 45531.2264 | 0.012494 | 0.00015815 | 99 | 7821 | Planned | Planned
1664 |  | 35778 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-08-27 | 45531.3333 | 2024-08-27 | 45531.634 | 0.085079 | 0.00019649 | 123 | 53259 | Planned | Planned
1665 |  | 35779 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-08-27 | 45531.3333 | 2024-08-27 | 45531.6882 | 0.11918 | 0.00023323 | 146 | 74606 | Planned | Planned
1666 |  | 35781 | HOBV K08 - K08 LUCKENS RD | Northern | HOBV K08 | 2024-08-27 | 45531.3958 | 2024-08-27 | 45531.5528 | 0.024911 | 0.00011022 | 69 | 15594 | Planned | Planned
1667 |  | 35782 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-08-27 | 45531.3854 | 2024-08-27 | 45531.7819 | 0.042871 | 7.5081e-05 | 47 | 26837 | Planned | Planned
1668 |  | 35783 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-08-27 | 45531.3785 | 2024-08-27 | 45531.6674 | 0.14886 | 0.00035783 | 224 | 93184 | Planned | Planned
1669 |  | 35784 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-08-27 | 45531.4715 | 2024-08-27 | 45531.5819 | 0.071859 | 0.00062137 | 389 | 44983 | Unplanned | Wildlife
1670 |  | 35785 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-08-27 | 45531.3653 | 2024-08-27 | 45531.5729 | 0.02627 | 8.7859e-05 | 55 | 16445 | Unplanned | Vegetation
1671 |  | 35786 | BUSH K04 - K04 UNSWORTH DRIVE | Northern | BUSH K04 | 2024-08-27 | 45531.8562 | 2024-08-27 | 45531.8785 | 0.00025559 | 7.987e-06 | 5 | 160 | Planned | Planned
1672 |  | 35787 | WOOD K02 - K02 SEL PEACOCK DR | Northern | WOOD K02 | 2024-08-28 | 45532.1875 | 2024-08-28 | 45532.2361 | 0.013697 | 0.00027796 | 174 | 8574 | Planned | Planned
1673 |  | 35788 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2024-08-27 | 45531.9583 | 2024-08-28 | 45532.0326 | 0.007179 | 6.7093e-05 | 42 | 4494 | Planned | Planned
1674 |  | 35789 | MKAU K22 - K22 MCDONALDS | Auckland | MKAU K22N | 2024-08-28 | 45532.0833 | 2024-08-28 | 45532.191 | 0.0044569 | 2.8754e-05 | 18 | 2790 | Planned | Planned
1675 |  | 35790 | RIVE K10 - K10 HUAPAI | Northern | RIVE K10 | 2024-08-28 | 45532.3333 | 2024-08-28 | 45532.6882 | 0.17306 | 0.00033866 | 212 | 108332 | Planned | Planned
1676 |  | 35791 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-08-28 | 45532.3799 | 2024-08-28 | 45532.6993 | 0.019106 | 4.1533e-05 | 26 | 11960 | Planned | Planned
1677 |  | 35792 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-08-28 | 45532.4444 | 2024-08-28 | 45532.6681 | 0.11316 | 0.00035144 | 220 | 70840 | Planned | Planned
1678 |  | 35793 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-08-28 | 45532.6965 | 2024-08-28 | 45532.7431 | 0.00021406 | 3.195e-06 | 2 | 134 | Unplanned | Wildlife
1679 |  | 35794 | ROSE K09 - K09 ALUMINIUM ANODISERS | Auckland | ROSE K09 | 2024-08-28 | 45532.9583 | 2024-08-29 | 45533.0417 | 0.0080512 | 6.7093e-05 | 42 | 5040 | Planned | Planned
1680 |  | 35795 | HOWI K16 - K16 PAKURANGA RD (497) | Auckland | HOWI K16 | 2024-08-28 | 45532.9799 | 2024-08-29 | 45533.2222 | 0.036796 | 0.00010543 | 66 | 23034 | Planned | Planned
1681 |  | 35796 | MCEN K12 - K12 ROBERTSON ROAD SOUTH | Auckland | MCEN K12 | 2024-08-29 | 45533.0833 | 2024-08-29 | 45533.1583 | 0.016562 | 0.00015336 | 96 | 10368 | Planned | Planned
1682 |  | 35797 | MWEL K01 - K01 MALONE RD | Auckland | MWEL K01 | 2024-08-29 | 45533.1667 | 2024-08-29 | 45533.1806 | 0.003163 | 0.00015815 | 99 | 1980 | Planned | Planned
1683 |  | 35798 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-08-29 | 45533.3549 | 2024-08-29 | 45533.6764 | 0.044377 | 9.5841e-05 | 60 | 27780 | Planned | Planned
1684 |  | 35799 | SHOW K05 - K05 LITTEN RD | Auckland | SHOW K05 | 2024-08-29 | 45533.4035 | 2024-08-29 | 45533.6806 | 0.038243 | 9.5848e-05 | 60 | 23940 | Planned | Planned
1685 |  | 35800 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-08-29 | 45533.6396 | 2024-08-29 | 45533.7549 | 0.070491 | 0.00069009 | 432 | 44127 | Unplanned | Cause unknown
1686 |  | 35804 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-08-29 | 45533.8396 | 2024-08-30 | 45534.1319 | 0.13661 | 0.0024745 | 828 | 85514 | Unplanned | Lightning
1687 |  | 35804 | WARK K04 - K04 LIME WORKS | Northern | WARK K13 | 2024-08-29 | 45533.8396 | 2024-08-30 | 45534.1319 | 0.00022364 | 5.591e-05 | 35 | 140 | Unplanned | Lightning
1688 |  | 35805 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-08-29 | 45533.7861 | 2024-08-29 | 45533.8451 | 0.00040735 | 4.791e-06 | 3 | 255 | Unplanned | Cause unknown
1689 |  | 35806 | HVAL K03 - K03 BRUCE McLAREN | Northern | HVAL K03 | 2024-08-29 | 45533.875 | 2024-08-30 | 45534.0104 | 0.0028035 | 1.4377e-05 | 9 | 1755 | Planned | Planned
1690 |  | 35807 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-08-29 | 45533.7306 | 2024-08-29 | 45533.8375 | 0.00024601 | 1.597e-06 | 1 | 154 | Unplanned | Lightning
1691 |  | 35808 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-29 | 45533.8354 | 2024-08-30 | 45534.0243 | 0.0021725 | 7.987e-06 | 5 | 1360 | Unplanned | Lightning
1692 |  | 35809 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-29 | 45533.8535 | 2024-08-30 | 45534.5576 | 0.0016198 | 1.597e-06 | 1 | 1014 | Unplanned | Lightning
1693 |  | 35810 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-08-29 | 45533.841 | 2024-08-30 | 45534.5924 | 0.041483 | 3.8339e-05 | 24 | 25968 | Unplanned | Lightning
1694 |  | 35811 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-29 | 45533.8354 | 2024-08-30 | 45534.1792 | 0.0015815 | 3.195e-06 | 2 | 990 | Unplanned | Lightning
1695 |  | 35812 | OTAR K02 - K02 MURCHISON RD | Auckland | OTAR K02 | 2024-08-30 | 45534.2153 | 2024-08-30 | 45534.2167 | 0.00045048 | 0.00022524 | 141 | 282 | Unplanned | Human error
1696 |  | 35813 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-08-30 | 45534.3542 | 2024-08-30 | 45534.659 | 0.052596 | 0.00011981 | 75 | 32925 | Planned | Planned
1697 |  | 35814 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-08-30 | 45534.0583 | 2024-08-30 | 45534.4368 | 0.0043531 | 7.987e-06 | 5 | 2725 | Unplanned | Lightning
1698 |  | 35815 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-30 | 45534.616 | 2024-08-31 | 45535.6493 | 0.0040256 | 1.4377e-05 | 9 | 2520 | Unplanned | Lightning
1699 |  | 35816 | SHOW K10 - K10 CULVER TERRACE | Auckland | SHOW K10 | 2024-08-30 | 45534.8354 | 2024-08-30 | 45534.9604 | 0.27072 | 0.0021933 | 1373 | 169468 | Unplanned | Defective equipment
1700 |  | 35817 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-30 | 45534.6306 | 2024-08-30 | 45534.9097 | 0.00064218 | 1.597e-06 | 1 | 402 | Unplanned | Lightning
1701 |  | 35818 | MARA K11 - K11 CRAIG RD | Auckland | MARA K11 | 2024-08-30 | 45534.9632 | 2024-08-31 | 45535.0618 | 0.04167 | 0.00029553 | 185 | 26085 | Planned | Planned
1702 |  | 35819 | REMU K19 - K19 ENTRICAN AVE 21 | Auckland | REMU K19 | 2024-08-30 | 45534.9583 | 2024-08-31 | 45535.2771 | 0.029329 | 6.3898e-05 | 40 | 18360 | Planned | Planned
1703 |  | 35820 | OTAR K17 - K17 GERALDINE AVE | Auckland | OTAR K17 | 2024-08-30 | 45534.9583 | 2024-08-31 | 45535.2139 | 0.046441 | 0.0001262 | 79 | 29072 | Planned | Planned
1704 |  | 35821 | SHOW K10 - K10 CULVER TERRACE | Auckland | SHOW K10 | 2024-08-31 | 45535.1667 | 2024-08-31 | 45535.2188 | 0.0022764 | 3.0352e-05 | 19 | 1425 | Unplanned | Cause unknown
1705 |  | 35822 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-08-31 | 45535.3549 | 2024-08-31 | 45535.7139 | 0.23868 | 0.00046166 | 289 | 149413 | Planned | Planned
1706 |  | 35824 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2024-08-31 | 45535.375 | 2024-08-31 | 45535.6993 | 0.12682 | 0.00027157 | 170 | 79390 | Planned | Planned
1707 |  | 35825 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-08-31 | 45535.4375 | 2024-08-31 | 45535.5813 | 0.16038 | 0.00077477 | 485 | 100395 | Planned | Planned
1708 |  | 35826 | WSWA K17 - K17 RICHARDSON RD O/H LINE WEST | Auckland | WSWA K17 | 2024-08-31 | 45535.4167 | 2024-08-31 | 45535.5847 | 0.049483 | 0.00020447 | 128 | 30976 | Unplanned | Defective equipment
1709 |  | 35827 | MANU K10 - K10 RUSSELL RD | Auckland | MANU K10 | 2024-08-31 | 45535.6104 | 2024-08-31 | 45535.6292 | 0.052433 | 0.0026789 | 1677 | 32823 | Unplanned | Third party interference
1710 |  | 35828 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-08-31 | 45535.6451 | 2024-08-31 | 45535.7694 | 0.00057189 | 3.195e-06 | 2 | 358 | Unplanned | Other Cause | Outage on Non-Vector asset
1711 |  | 35829 | MNAB K16 - K16 GLASS RECYCLERS | Auckland | MNAB K16 | 2024-08-31 | 45535.8333 | 2024-08-31 | 45535.9354 | 0.0079841 | 5.4313e-05 | 34 | 4998 | Planned | Planned
1712 |  | 35830 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-08-31 | 45535.8771 | 2024-09-01 | 45536.416 | 0.15413 | 0.0036774 | 2212 | 96485 | Unplanned | Third party interference
1713 |  | 35839 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-09-01 | 45536.0847 | 2024-09-02 | 45537.8722 | 0.060732 | 0.00052877 | 305 | 38018 | Unplanned | Defective equipment
1714 |  | 35846 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-01 | 45536.0785 | 2024-09-01 | 45536.2431 | 0.04752 | 0.00033068 | 207 | 29747 | Unplanned | Lightning
1715 |  | 35848 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-09-01 | 45536.1167 | 2024-09-01 | 45536.1958 | 0.0096487 | 0.00057987 | 363 | 6040 | Unplanned | Cause unknown
1716 |  | 35857 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-01 | 45536.1389 | 2024-09-01 | 45536.2326 | 0.00043131 | 3.195e-06 | 2 | 270 | Unplanned | Lightning
1717 |  | 35858 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-09-01 | 45536.0813 | 2024-09-01 | 45536.2465 | 0.0011406 | 4.792e-06 | 3 | 714 | Unplanned | Lightning
1718 |  | 35859 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-01 | 45536.1389 | 2024-09-01 | 45536.5229 | 0.0035336 | 6.39e-06 | 4 | 2212 | Unplanned | Lightning
1719 |  | 35860 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-01 | 45536.2937 | 2024-09-01 | 45536.4194 | 0.059852 | 0.00033066 | 207 | 37467 | Unplanned | Vegetation
1720 |  | 35861 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-09-01 | 45536.241 | 2024-09-01 | 45536.366 | 0.0011022 | 6.391e-06 | 4 | 690 | Unplanned | Lightning
1721 |  | 35862 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-01 | 45536.1035 | 2024-09-02 | 45537.7222 | 0.068004 | 0.0003738 | 234 | 42570 | Unplanned | Lightning
1722 |  | 35863 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-09-01 | 45536.1069 | 2024-09-01 | 45536.8861 | 0.0035847 | 3.195e-06 | 2 | 2244 | Unplanned | Lightning
1723 |  | 35864 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.1042 | 2024-09-01 | 45536.3785 | 0.003155 | 7.987e-06 | 5 | 1975 | Unplanned | Other Cause | Outage on Non-Vector asset
1724 |  | 35865 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.3681 | 2024-09-01 | 45536.7868 | 0.011559 | 1.917e-05 | 12 | 7236 | Unplanned | Lightning
1725 |  | 35866 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-01 | 45536.1326 | 2024-09-02 | 45537.7986 | 0.0076646 | 3.195e-06 | 2 | 4798 | Unplanned | Lightning
1726 |  | 35867 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-09-01 | 45536.4222 | 2024-09-01 | 45536.4597 | 0.0043994 | 8.1464e-05 | 51 | 2754 | Unplanned | Cause unknown
1727 |  | 35868 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-09-01 | 45536.25 | 2024-09-01 | 45536.4299 | 0.001655 | 6.39e-06 | 4 | 1036 | Unplanned | Vegetation
1728 |  | 35869 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-01 | 45536.1083 | 2024-09-01 | 45536.4757 | 0.00084506 | 1.597e-06 | 1 | 529 | Unplanned | Lightning
1729 |  | 35870 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-01 | 45536.3153 | 2024-09-01 | 45536.5035 | 0.00043291 | 1.597e-06 | 1 | 271 | Unplanned | Lightning
1730 |  | 35871 | HELE K10 - K10 KAUKAPAKAPA | Northern | HELE K10 | 2024-09-01 | 45536.3625 | 2024-09-01 | 45536.5868 | 0.001032 | 3.194e-06 | 2 | 646 | Unplanned | Lightning
1731 |  | 35872 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-01 | 45536.1174 | 2024-09-01 | 45536.5382 | 0.0058084 | 9.585e-06 | 6 | 3636 | Unplanned | Lightning
1732 |  | 35873 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-09-01 | 45536.2806 | 2024-09-01 | 45536.5437 | 0.0012109 | 3.195e-06 | 2 | 758 | Unplanned | Lightning
1733 |  | 35874 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.541 | 2024-09-02 | 45537.5653 | 0.0047125 | 3.195e-06 | 2 | 2950 | Unplanned | Lightning
1734 |  | 35875 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-01 | 45536.3271 | 2024-09-01 | 45536.5153 | 0.0017316 | 6.39e-06 | 4 | 1084 | Unplanned | Lightning
1735 |  | 35876 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-01 | 45536.3944 | 2024-09-01 | 45536.6174 | 0.00051278 | 1.597e-06 | 1 | 321 | Unplanned | Cause unknown
1736 |  | 35877 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.4208 | 2024-09-01 | 45536.6097 | 0.00043451 | 1.597e-06 | 1 | 272 | Unplanned | Cause unknown
1737 |  | 35878 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-01 | 45536.4875 | 2024-09-01 | 45536.5104 | 5.2716e-05 | 1.597e-06 | 1 | 33 | Unplanned | Cause unknown
1738 |  | 35879 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-09-01 | 45536.3882 | 2024-09-01 | 45536.6146 | 0.00052077 | 1.597e-06 | 1 | 326 | Unplanned | Cause unknown
1739 |  | 35880 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-01 | 45536.1542 | 2024-09-01 | 45536.6236 | 0.0032396 | 4.792e-06 | 3 | 2028 | Unplanned | Lightning
1740 |  | 35881 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-01 | 45536.6007 | 2024-09-01 | 45536.6521 | 0.00011821 | 1.597e-06 | 1 | 74 | Unplanned | Cause unknown
1741 |  | 35882 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.6889 | 2024-09-02 | 45537.5757 | 0.00037381 | 6.39e-06 | 2 | 234 | Unplanned | Lightning
1742 |  | 35883 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-01 | 45536.6514 | 2024-09-01 | 45536.7431 | 0.00084346 | 6.389e-06 | 4 | 528 | Unplanned | Lightning
1743 |  | 35884 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-01 | 45536.1736 | 2024-09-02 | 45537.6028 | 0.01315 | 6.39e-06 | 4 | 8232 | Unplanned | Lightning
1744 |  | 35885 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.3799 | 2024-09-01 | 45536.7021 | 0.00074122 | 1.597e-06 | 1 | 464 | Unplanned | Cause unknown
1745 |  | 35886 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-01 | 45536.5125 | 2024-09-01 | 45536.7236 | 0.00048563 | 1.597e-06 | 1 | 304 | Unplanned | Lightning
1746 |  | 35887 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-09-01 | 45536.3083 | 2024-09-02 | 45537.7792 | 0.0067668 | 3.195e-06 | 2 | 4236 | Unplanned | Lightning
1747 |  | 35888 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-01 | 45536.7299 | 2024-09-01 | 45536.9 | 0.0019569 | 7.987e-06 | 5 | 1225 | Unplanned | Lightning
1748 |  | 35890 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-09-01 | 45536.9792 | 2024-09-02 | 45537.075 | 0.010361 | 7.508e-05 | 47 | 6486 | Planned | Planned
1749 |  | 35891 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-01 | 45536.766 | 2024-09-01 | 45536.9722 | 0.00094889 | 3.195e-06 | 2 | 594 | Unplanned | Lightning
1750 |  | 35893 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-09-01 | 45536.5646 | 2024-09-02 | 45537.8056 | 0.008564 | 4.792e-06 | 3 | 5361 | Unplanned | Lightning
1751 |  | 35894 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-01 | 45536.916 | 2024-09-02 | 45537.9153 | 0.009195 | 6.39e-06 | 4 | 5756 | Unplanned | Lightning
1752 |  | 35895 | BMON K04 - K04 GRAMMAR SCHOOL + LS | Northern | BMON K04 | 2024-09-02 | 45537.1792 | 2024-09-02 | 45537.9951 | 0.25206 | 0.0013067 | 463 | 157785 | Unplanned | Third party interference
1753 |  | 35896 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-01 | 45536.575 | 2024-09-02 | 45537.8132 | 0.014241 | 7.987e-06 | 5 | 8915 | Unplanned | Lightning
1754 |  | 35897 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-01 | 45536.7403 | 2024-09-02 | 45537.7986 | 0.021614 | 9.4246e-05 | 59 | 13530 | Unplanned | Lightning
1755 |  | 35898 | HILL K07 - K07 173 HILLSBOROUGH RD | Auckland | HILL K07 | 2024-09-02 | 45537.2097 | 2024-09-02 | 45537.6632 | 0.12726 | 0.00019489 | 122 | 79666 | Unplanned | Third party interference
1756 |  | 35899 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-02 | 45537.2882 | 2024-09-02 | 45537.391 | 0.0009457 | 6.39e-06 | 4 | 592 | Unplanned | Cause unknown
1757 |  | 35900 | SAND K13 - K13 2 MAYN AVE | Auckland | SAND K13 | 2024-08-24 | 45528.9174 | 2024-08-25 | 45529.1965 | 0.0025687 | 6.39e-06 | 4 | 1608 | Planned | Planned
1758 |  | 35901 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-02 | 45537.2069 | 2024-09-02 | 45537.4132 | 0.00094889 | 3.195e-06 | 2 | 594 | Unplanned | Cause unknown
1759 |  | 35902 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-09-02 | 45537.3049 | 2024-09-03 | 45538.5903 | 0.0059138 | 3.195e-06 | 2 | 3702 | Unplanned | Lightning
1760 |  | 35903 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-02 | 45537.15 | 2024-09-02 | 45537.4583 | 0.0028371 | 6.39e-06 | 4 | 1776 | Unplanned | Cause unknown
1761 |  | 35904 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.6618 | 2024-09-02 | 45537.4757 | 0.0018722 | 1.597e-06 | 1 | 1172 | Unplanned | Defective equipment
1762 |  | 35905 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-09-01 | 45536.9903 | 2024-09-03 | 45538.7611 | 0.012221 | 4.792e-06 | 3 | 7650 | Unplanned | Lightning
1763 |  | 35907 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-02 | 45537.2951 | 2024-09-02 | 45537.5146 | 0.0010096 | 3.195e-06 | 2 | 632 | Unplanned | Cause unknown
1764 |  | 35908 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-02 | 45537.5132 | 2024-09-02 | 45537.5424 | 0.00013419 | 3.195e-06 | 2 | 84 | Unplanned | Cause unknown
1765 |  | 35909 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-02 | 45537.6424 | 2024-09-02 | 45537.8438 | 0.0013898 | 4.792e-06 | 3 | 870 | Unplanned | Defective equipment
1766 |  | 35910 | PAPA K01 - K01 SETTLEMENT RD | Auckland | PAPA K01 | 2024-09-02 | 45537.5785 | 2024-09-02 | 45537.6764 | 0.00022524 | 1.597e-06 | 1 | 141 | Unplanned | Cause unknown
1767 |  | 35911 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-09-02 | 45537.6771 | 2024-09-02 | 45537.6944 | 0.00015975 | 6.39e-06 | 4 | 100 | Unplanned | Defective equipment
1768 |  | 35912 | OTAR K13 - K13 ORMISTON RD SW/STN | Auckland | OTAR K13 | 2024-09-02 | 45537.8958 | 2024-09-03 | 45538.1896 | 0.045274 | 0.00010703 | 67 | 28341 | Planned | Planned
1769 |  | 35913 | AVON K01 - K01 BLOCKHOUSE BAY RD.(353) | Auckland | AVON K01 | 2024-09-02 | 45537.9583 | 2024-09-03 | 45538.0674 | 0.073736 | 0.00046965 | 294 | 46158 | Planned | Planned
1770 |  | 35914 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-02 | 45537.8535 | 2024-09-03 | 45538.5778 | 0.0049984 | 4.792e-06 | 3 | 3129 | Unplanned | Lightning
1771 |  | 35915 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-02 | 45537.9139 | 2024-09-03 | 45538.0069 | 0.00085624 | 6.39e-06 | 4 | 536 | Unplanned | Lightning
1772 |  | 35916 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | AVON K03 | 2024-09-03 | 45538.1042 | 2024-09-03 | 45538.1993 | 0.011499 | 9.425e-05 | 59 | 7198 | Planned | Planned
1773 |  | 35916 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | ROSE K05 | 2024-09-03 | 45538.1042 | 2024-09-03 | 45538.1993 | 0.014007 | 0.00010224 | 64 | 8768 | Planned | Planned
1774 |  | 35917 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-09-03 | 45538.2083 | 2024-09-03 | 45538.3097 | 0.029465 | 0.00021723 | 136 | 18445 | Planned | Planned
1775 |  | 35918 | ROCK K21 - K21 MT SMART No.2 | Auckland | ROCK K21 | 2024-09-03 | 45538.3 | 2024-09-03 | 45538.4097 | 0.0005048 | 3.195e-06 | 2 | 316 | Planned | Planned
1776 |  | 35919 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-09-03 | 45538.3444 | 2024-09-03 | 45538.6875 | 0.053485 | 0.00011822 | 74 | 33481 | Planned | Planned
1777 |  | 35921 | KING K19 - K19 SUMMIT HOLDINGS | Auckland | KING K19 | 2024-09-03 | 45538.3958 | 2024-09-03 | 45538.6875 | 0.073132 | 0.00017412 | 109 | 45780 | Planned | Planned
1778 |  | 35922 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-03 | 45538.2979 | 2024-09-03 | 45538.3597 | 0.00071087 | 7.986e-06 | 5 | 445 | Unplanned | Cause unknown
1779 |  | 35923 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-03 | 45538.3681 | 2024-09-03 | 45538.8646 | 0.0022844 | 3.195e-06 | 2 | 1430 | Unplanned | Defective equipment
1780 |  | 35924 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-03 | 45538.3389 | 2024-09-03 | 45538.9028 | 0.0012971 | 1.597e-06 | 1 | 812 | Unplanned | Defective equipment
1781 |  | 35925 | MALB K17 - K17 ALLENDALE RD | Auckland | MALB K17 | 2024-09-03 | 45538.5597 | 2024-09-04 | 45539.2465 | 0.35617 | 0.0010943 | 387 | 222959 | Unplanned | Third party interference
1782 |  | 35926 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-03 | 45538.5514 | 2024-09-03 | 45538.5576 | 0.00015815 | 1.7572e-05 | 11 | 99 | Unplanned | Third party interference
1783 |  | 35927 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-03 | 45538.566 | 2024-09-03 | 45538.7264 | 0.001107 | 4.792e-06 | 3 | 693 | Unplanned | Defective equipment
1784 |  | 35928 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-03 | 45538.566 | 2024-09-04 | 45539.5889 | 0.0070592 | 4.792e-06 | 3 | 4419 | Unplanned | Lightning
1785 |  | 35929 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-09-03 | 45538.5472 | 2024-09-03 | 45538.6076 | 0.00041694 | 4.792e-06 | 3 | 261 | Unplanned | Vegetation
1786 |  | 35930 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-03 | 45538.6431 | 2024-09-03 | 45538.7069 | 0.00014697 | 1.597e-06 | 1 | 92 | Unplanned | Lightning
1787 |  | 35931 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-09-03 | 45538.7444 | 2024-09-04 | 45539.359 | 0.021064 | 0.00062938 | 394 | 13186 | Unplanned | Third party interference
1788 |  | 35932 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-03 | 45538.6861 | 2024-09-04 | 45539.8125 | 0.0039202 | 7.988e-06 | 5 | 2454 | Unplanned | Defective equipment
1789 |  | 35933 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-03 | 45538.8174 | 2024-09-03 | 45538.8493 | 7.3483e-05 | 1.597e-06 | 1 | 46 | Unplanned | Defective equipment
1790 |  | 35934 | DRIV K06 - K06 EVE'S EPSOM | Auckland | DRIV K06 | 2024-09-03 | 45538.8257 | 2024-09-03 | 45538.9917 | 0.1428 | 0.0010719 | 671 | 89389 | Unplanned | Third party interference
1791 |  | 35936 | ONEH K12 - K12 - SELWYN ST SOUTH + LS | Auckland | ONEH K12 | 2024-09-04 | 45539.0722 | 2024-09-04 | 45539.0938 | 0.04452 | 0.0014361 | 899 | 27869 | Unplanned | Third party interference
1792 |  | 35938 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-09-04 | 45539.3542 | 2024-09-04 | 45539.7264 | 0.38146 | 0.0007125 | 446 | 238790 | Planned | Planned
1793 |  | 35939 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-04 | 45539.3979 | 2024-09-04 | 45539.4861 | 0.00040575 | 3.195e-06 | 2 | 254 | Unplanned | Lightning
1794 |  | 35940 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-09-04 | 45539.4375 | 2024-09-04 | 45539.5208 | 0.0001917 | 1.597e-06 | 1 | 120 | Unplanned | Lightning
1795 |  | 35941 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-04 | 45539.5076 | 2024-09-04 | 45539.5382 | 7.0288e-05 | 1.597e-06 | 1 | 44 | Unplanned | Lightning
1796 |  | 35942 | ROCK K15 - K15 MAROA RD | Auckland | ROCK K15 | 2024-09-04 | 45539.75 | 2024-09-04 | 45539.9674 | 0.059001 | 0.0001885 | 118 | 36934 | Unplanned | Third party interference
1797 |  | 35943 | SUNS K01 - K01 LANDSBERG WAY | Northern | SUNS K01 | 2024-09-04 | 45539.9375 | 2024-09-05 | 45540.1438 | 0.11814 | 0.00039777 | 249 | 73953 | Planned | Planned
1798 |  | 35944 | NEWM K01 - K01 EDUCATIONAL DEPT VIA LS | Auckland | NEWM K01 | 2024-09-04 | 45539.9583 | 2024-09-05 | 45540.0583 | 0.088333 | 0.00061342 | 384 | 55296 | Planned | Planned
1799 |  | 35945 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-09-05 | 45540.2083 | 2024-09-05 | 45540.2812 | 0.020478 | 0.00021406 | 134 | 12819 | Planned | Planned
1800 |  | 35946 | RDAL K08 - K08 COWLEY PL | Northern | RDAL K08 | 2024-09-05 | 45540.3333 | 2024-09-05 | 45540.5174 | 0.030056 | 0.00011342 | 71 | 18815 | Planned | Planned
1801 |  | 35947 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-09-05 | 45540.3333 | 2024-09-05 | 45540.7111 | 0.38902 | 0.00072046 | 451 | 243526 | Planned | Planned
1802 |  | 35948 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-09-05 | 45540.3785 | 2024-09-05 | 45540.6472 | 0.037711 | 9.7445e-05 | 61 | 23607 | Planned | Planned
1803 |  | 35949 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-09-05 | 45540.3958 | 2024-09-05 | 45540.5938 | 0.013658 | 4.7922e-05 | 30 | 8550 | Planned | Planned
1804 |  | 35950 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-05 | 45540.5069 | 2024-09-05 | 45540.6319 | 0.00057509 | 3.195e-06 | 2 | 360 | Unplanned | Lightning
1805 |  | 35951 | REMU K14 - K14 TAHORA AVE | Auckland | REMU K14 | 2024-09-05 | 45540.5458 | 2024-09-05 | 45540.8472 | 0.24098 | 0.0024521 | 876 | 150852 | Unplanned | Defective equipment
1806 |  | 35952 | ROCK K21 - K21 MT SMART No.2 | Auckland | ROCK K21 | 2024-09-05 | 45540.7521 | 2024-09-05 | 45540.825 | 0.00033547 | 3.195e-06 | 2 | 210 | Planned | Planned
1807 |  | 35953 | HAUR K01 - K01 BURNS AVENUE | Northern | HAUR K01 | 2024-09-05 | 45540.9257 | 2024-09-06 | 45541.3576 | 0.35417 | 0.0030671 | 878 | 221710 | Unplanned | Defective equipment
1808 |  | 35953 | HAUR K01 - K01 BURNS AVENUE | Northern | TAKP K11 | 2024-09-05 | 45540.9257 | 2024-09-06 | 45541.3576 | 0.057625 | 0.00031948 | 158 | 36073 | Unplanned | Defective equipment
1809 |  | 35954 | MEAS K15 - K15 RAGLAN ST VIA LOCAL SUB | Auckland | MEAS K15 | 2024-09-05 | 45540.9597 | 2024-09-06 | 45541.0569 | 0.013834 | 0.0013834 | 866 | 8660 | Unplanned | Cause unknown
1810 |  | 35954 | MEAS K15 - K15 RAGLAN ST VIA LOCAL SUB | Auckland | MEAS K19 | 2024-09-05 | 45540.9597 | 2024-09-06 | 45541.0569 | 0.068633 | 0.0027109 | 1697 | 42964 | Unplanned | Cause unknown
1811 |  | 35955 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-09-05 | 45540.9792 | 2024-09-06 | 45541.1347 | 0.0010735 | 4.792e-06 | 3 | 672 | Planned | Planned
1812 |  | 35956 | HOWI K16 - K16 PAKURANGA RD (497) | Auckland | HOWI K16 | 2024-09-05 | 45540.9792 | 2024-09-06 | 45541.2292 | 0.037956 | 0.00010543 | 66 | 23760 | Planned | Planned
1813 |  | 35957 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-09-06 | 45541.375 | 2024-09-06 | 45541.6715 | 0.062072 | 0.00014536 | 91 | 38857 | Planned | Planned
1814 |  | 35958 | NEWM K02 - K02 BROADWAY CENTRE | Auckland | NEWM K02 | 2024-09-06 | 45541.4167 | 2024-09-06 | 45541.6986 | 0.062263 | 0.00015336 | 96 | 38976 | Planned | Planned
1815 |  | 35959 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2024-09-06 | 45541.4424 | 2024-09-06 | 45541.6715 | 0.17802 | 0.00087061 | 545 | 111442 | Unplanned | Defective equipment
1816 |  | 35960 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-09-06 | 45541.4257 | 2024-09-06 | 45541.6062 | 0.0075176 | 3.0352e-05 | 19 | 4706 | Planned | Planned
1817 |  | 35961 | GHIT K02 - K02 ORWELL RD | Northern | GHIT K02 | 2024-09-06 | 45541.6132 | 2024-09-06 | 45541.684 | 0.0277 | 0.00027157 | 170 | 17340 | Unplanned | Third party interference
1818 |  | 35962 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2024-09-06 | 45541.6903 | 2024-09-06 | 45541.7444 | 0.0048595 | 6.2301e-05 | 39 | 3042 | Unplanned | Cause unknown
1819 |  | 35963 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-09-06 | 45541.7986 | 2024-09-07 | 45542.2812 | 0.058842 | 8.4665e-05 | 53 | 36835 | Planned | Planned
1820 |  | 35964 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-09-06 | 45541.7917 | 2024-09-06 | 45541.825 | 0.019553 | 0.00040735 | 255 | 12240 | Unplanned | Defective equipment
1821 |  | 35965 | ROSE K06 - K06 COPSEY PL | Auckland | ROSE K06 | 2024-09-06 | 45541.9167 | 2024-09-06 | 45541.9896 | 0.00033547 | 3.195e-06 | 2 | 210 | Planned | Planned
1822 |  | 35966 | ROCK K13 - K13 GREENPARK RD | Auckland | ROCK K13 | 2024-09-07 | 45542 | 2024-09-07 | 45542.1743 | 0.0068164 | 2.7156e-05 | 17 | 4267 | Planned | Planned
1823 |  | 35967 | CLEN K07 - K07 ROBERT ROSS | Auckland | CLEN K07 | 2024-09-06 | 45541.934 | 2024-09-07 | 45542.2014 | 0.042437 | 0.00011022 | 69 | 26565 | Unplanned | Defective equipment
1824 |  | 35968 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-09-07 | 45542.3333 | 2024-09-07 | 45542.7396 | 0.0079697 | 1.4377e-05 | 9 | 4989 | Planned | Planned
1825 |  | 35969 | RDAL K05 - K05 APOLLO DR AND LOCAL SERVICE | Northern | RDAL K05 | 2024-09-07 | 45542.3368 | 2024-09-07 | 45542.7014 | 0.002516 | 4.792e-06 | 3 | 1575 | Planned | Planned
1826 |  | 35970 | MKAU K23 - K23 GREAT SOUTH ROAD | Auckland | MKAU K23 | 2024-09-07 | 45542.3458 | 2024-09-07 | 45542.3694 | 0.056649 | 0.0016662 | 1043 | 35462 | Unplanned | Third party interference
1827 |  | 35971 | PAPA K09 - K09 LAURIE AVE | Auckland | PAPA K09 | 2024-09-07 | 45542.384 | 2024-09-07 | 45542.6903 | 0.039451 | 8.9458e-05 | 56 | 24696 | Planned | Planned
1828 |  | 35972 | WEST K09 - K09 TELSTRA SATURN | Auckland | WEST K09 | 2024-09-07 | 45542.3792 | 2024-09-07 | 45542.7417 | 0.00083387 | 1.597e-06 | 1 | 522 | Planned | Planned
1829 |  | 35974 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-09-07 | 45542.6222 | 2024-09-07 | 45542.7208 | 0.0027221 | 1.9169e-05 | 12 | 1704 | Unplanned | Cause unknown
1830 |  | 35975 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-07 | 45542.8993 | 2024-09-07 | 45542.9896 | 0.016198 | 0.0001246 | 78 | 10140 | Unplanned | Defective equipment
1831 |  | 35976 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-09-08 | 45543.0535 | 2024-09-08 | 45543.1278 | 0.03675 | 0.00034345 | 215 | 23005 | Unplanned | Vegetation
1832 |  | 35978 | SABU K02 - K02 HEPBURN RD | Northern | SABU K02 | 2024-09-08 | 45543.4549 | 2024-09-08 | 45543.5222 | 0.052293 | 0.0016566 | 1037 | 32735 | Unplanned | Cause unknown
1833 |  | 35979 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K05 | 2024-09-08 | 45543.9583 | 2024-09-09 | 45544.0569 | 0.027901 | 0.00019649 | 123 | 17466 | Planned | Planned
1834 |  | 35979 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K13 | 2024-09-08 | 45543.9583 | 2024-09-09 | 45544.0569 | 0.061473 | 0.00043291 | 271 | 38482 | Planned | Planned
1835 |  | 35980 | PARN K11 - K11 BONNICI MOTORS VIA SW/STN | Auckland | PARN K11 | 2024-09-09 | 45544.0424 | 2024-09-09 | 45544.1097 | 0.018439 | 0.0001901 | 119 | 11543 | Planned | Planned
1836 |  | 35982 | TAKP K11 - K11 NORTHCROFT STREET | Northern | TAKP K11 | 2024-09-08 | 45543.8764 | 2024-09-08 | 45543.9007 | 0.00016773 | 4.792e-06 | 3 | 105 | Planned | Planned
1837 |  | 35984 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-09-09 | 45544.4479 | 2024-09-09 | 45544.534 | 0.0085177 | 6.8691e-05 | 43 | 5332 | Planned | Planned
1838 |  | 35986 | PAPA K01 - K01 SETTLEMENT RD | Auckland | PAPA K01 | 2024-09-09 | 45544.4243 | 2024-09-09 | 45544.4917 | 0.00015495 | 1.597e-06 | 1 | 97 | Unplanned | Cause unknown
1839 |  | 35987 | TAKA K13 - K13 COSGROVE RD | Auckland | TAKA K13 | 2024-09-09 | 45544.6472 | 2024-09-10 | 45545.275 | 0.43639 | 0.0034218 | 1649 | 273179 | Unplanned | Third party interference
1840 |  | 35988 | GREE K20 - K20 ALERT ENGINEERING | Auckland | GREE K20 | 2024-09-09 | 45544.7694 | 2024-09-09 | 45544.8319 | 0.1157 | 0.0013243 | 829 | 72430 | Unplanned | Defective equipment
1841 |  | 35989 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-09 | 45544.7812 | 2024-09-09 | 45544.8368 | 0.00025559 | 3.195e-06 | 2 | 160 | Unplanned | Defective equipment
1842 |  | 35990 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-09-09 | 45544.9583 | 2024-09-10 | 45545.0458 | 0.0032205 | 2.5559e-05 | 16 | 2016 | Planned | Planned
1843 |  | 35991 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-09-10 | 45545.0833 | 2024-09-10 | 45545.1687 | 0.0053052 | 4.3131e-05 | 27 | 3321 | Planned | Planned
1844 |  | 35992 | ATKI K09 - K09 KAURILANDS RD | Northern | ATKI K09 | 2024-09-10 | 45545.334 | 2024-09-10 | 45545.7278 | 0.25814 | 0.00045527 | 285 | 161595 | Planned | Planned
1845 |  | 35993 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-09-10 | 45545.3333 | 2024-09-10 | 45545.634 | 0.0006917 | 1.597e-06 | 1 | 433 | Planned | Planned
1846 |  | 35994 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-09-10 | 45545.375 | 2024-09-10 | 45545.6472 | 0.10082 | 0.00025719 | 161 | 63112 | Planned | Planned
1847 |  | 35995 | FBSH K05 - K05 WISTERIA LANE | Auckland | FBSH K05 | 2024-09-10 | 45545.375 | 2024-09-10 | 45545.6729 | 0.0047684 | 1.1182e-05 | 7 | 2985 | Planned | Planned
1848 |  | 35996 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-09-10 | 45545.375 | 2024-09-10 | 45545.7111 | 0.019329 | 3.9935e-05 | 25 | 12100 | Planned | Planned
1849 |  | 35997 | BLMN K02 - K02 GLENWOOD AVE | Northern | BLMN K02 | 2024-09-10 | 45545.3771 | 2024-09-10 | 45545.7701 | 0.2251 | 0.00077477 | 371 | 140911 | Planned | Planned
1850 |  | 35998 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-09-10 | 45545.3958 | 2024-09-10 | 45545.525 | 0.045194 | 0.00026358 | 165 | 28291 | Planned | Planned
1851 |  | 35999 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-10 | 45545.4167 | 2024-09-10 | 45545.6875 | 0.002492 | 6.39e-06 | 4 | 1560 | Planned | Planned
1852 |  | 36000 | SJOH K09 - K09 168 NORMAN LESSER DR | Auckland | SJOH K09 | 2024-09-10 | 45545.9792 | 2024-09-11 | 45546.1528 | 0.029553 | 0.00011821 | 74 | 18500 | Planned | Planned
1853 |  | 36001 | GREE K19 - K19 TI RAKAU CENTRE | Auckland | GREE K19 | 2024-09-10 | 45545.9826 | 2024-09-11 | 45546.2104 | 0.024626 | 7.5081e-05 | 47 | 15416 | Planned | Planned
1854 |  | 36002 | NSBT109 - HOBSONVILLE P780 û CDC HOBSONVILLE H08 (109) | Northern | HOBV K10 | 2024-09-11 | 45546.3542 | 2024-09-11 | 45546.725 | 0.17573 | 0.00032908 | 206 | 110004 | Planned | Planned
1855 |  | 36003 | BUSH K02 - K02 ARMSTRONG RD | Northern | BUSH K02 | 2024-09-11 | 45546.3806 | 2024-09-11 | 45546.5243 | 0.00066135 | 3.194e-06 | 2 | 414 | Planned | Planned
1856 |  | 36004 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-09-11 | 45546.375 | 2024-09-11 | 45546.6507 | 0.00063419 | 1.597e-06 | 1 | 397 | Planned | Planned
1857 |  | 36005 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-11 | 45546.4014 | 2024-09-11 | 45546.6431 | 0.0011118 | 3.195e-06 | 2 | 696 | Planned | Planned
1858 |  | 36007 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-11 | 45546.4097 | 2024-09-11 | 45546.5097 | 0.0006901 | 4.792e-06 | 3 | 432 | Unplanned | Defective equipment
1859 |  | 36008 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-11 | 45546.3875 | 2024-09-11 | 45546.7986 | 0.032564 | 7.5075e-05 | 47 | 20385 | Planned | Planned
1860 |  | 36009 | WEST K09 - K09 TELSTRA SATURN | Auckland | WEST K09 | 2024-09-11 | 45546.9174 | 2024-09-12 | 45547.1632 | 0.01131 | 3.1949e-05 | 20 | 7080 | Planned | Planned
1861 |  | 36010 | SUNS K01 - K01 LANDSBERG WAY | Northern | SUNS K01 | 2024-09-11 | 45546.9792 | 2024-09-12 | 45547.1104 | 0.07548 | 0.00039936 | 250 | 47250 | Planned | Planned
1862 |  | 36011 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-09-11 | 45546.9583 | 2024-09-12 | 45547.0458 | 0.016505 | 0.00013099 | 82 | 10332 | Planned | Planned
1863 |  | 36012 | GINN K13 - K13 MELLING ST | Auckland | GINN K13 | 2024-09-12 | 45547.0833 | 2024-09-12 | 45547.1667 | 0.021853 | 0.00018211 | 114 | 13680 | Planned | Planned
1864 |  | 36014 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-09-12 | 45547.3542 | 2024-09-12 | 45547.7118 | 0.022213 | 4.3131e-05 | 27 | 13905 | Planned | Planned
1865 |  | 36015 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-09-12 | 45547.5576 | 2024-09-12 | 45547.7847 | 0.019695 | 0.00025239 | 158 | 12329 | Unplanned | Third party interference
1866 |  | 36017 | BUSH K09 - K09 ROTHWELL AVENUE | Northern | BUSH K09 | 2024-09-12 | 45547.875 | 2024-09-13 | 45548.0625 | 0.0025879 | 9.585e-06 | 6 | 1620 | Planned | Planned
1867 |  | 36018 | OREW K08 - K08 MARIE RD | Northern | OREW K08 | 2024-09-12 | 45547.875 | 2024-09-13 | 45548.2472 | 0.1036 | 0.00019329 | 121 | 64856 | Planned | Planned
1868 |  | 36019 | TAKP K11 - K11 NORTHCROFT STREET | Northern | TAKP K11 | 2024-09-12 | 45547.875 | 2024-09-13 | 45548.0146 | 0.014128 | 7.0288e-05 | 44 | 8844 | Planned | Planned
1869 |  | 36020 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-09-12 | 45547.8465 | 2024-09-12 | 45547.8958 | 0.00011342 | 1.597e-06 | 1 | 71 | Unplanned | Cause unknown
1870 |  | 36021 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-12 | 45547.9583 | 2024-09-13 | 45548.0743 | 0.054956 | 0.00032906 | 206 | 34402 | Planned | Planned
1871 |  | 36022 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-13 | 45548.0417 | 2024-09-13 | 45548.1389 | 0.0020128 | 1.4377e-05 | 9 | 1260 | Planned | Planned
1872 |  | 36023 | BIRK K02 - K02 DOMAIN ROAD | Northern | BIRK K02 | 2024-09-13 | 45548.3438 | 2024-09-13 | 45548.7465 | 0.28352 | 0.00048882 | 306 | 177480 | Planned | Planned
1873 |  | 36023 | BIRK K02 - K02 DOMAIN ROAD | Northern | BIRK K12 | 2024-09-13 | 45548.3438 | 2024-09-13 | 45548.7465 | 0.089062 | 0.00016134 | 101 | 55752 | Planned | Planned
1874 |  | 36024 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-09-13 | 45548.3771 | 2024-09-13 | 45548.7424 | 0.030249 | 5.7509e-05 | 36 | 18936 | Planned | Planned
1875 |  | 36025 | PAPA K01 - K01 SETTLEMENT RD | Auckland | PAPA K01 | 2024-09-13 | 45548.3861 | 2024-09-13 | 45548.4201 | 7.8276e-05 | 1.597e-06 | 1 | 49 | Unplanned | Third party interference
1876 |  | 36028 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-09-13 | 45548.959 | 2024-09-14 | 45549.2257 | 0.13925 | 0.00036262 | 227 | 87168 | Planned | Planned
1877 |  | 36031 | MKIN K11 - K11 THE AVENUE | Northern | MKIN K11 | 2024-09-14 | 45549.5368 | 2024-09-14 | 45549.6278 | 0.18445 | 0.0023371 | 1463 | 115465 | Unplanned | Defective equipment
1878 |  | 36032 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-09-14 | 45549.6146 | 2024-09-14 | 45549.6431 | 0.00019649 | 4.792e-06 | 3 | 123 | Unplanned | Defective equipment
1879 |  | 36034 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-09-15 | 45550.2056 | 2024-09-15 | 45550.7472 | 0.36462 | 0.006032 | 1957 | 228251 | Unplanned | Cause unknown
1880 |  | 36035 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-09-15 | 45550.2417 | 2024-09-15 | 45550.291 | 0.0019281 | 2.7157e-05 | 17 | 1207 | Unplanned | Cause unknown
1881 |  | 36036 | SYLV K15 - K15 25 CARBINE RD SW STN | Auckland | SYLV K15 | 2024-09-15 | 45550.375 | 2024-09-15 | 45550.5174 | 0.00032748 | 1.597e-06 | 1 | 205 | Planned | Planned
1882 |  | 36037 | WEST K12 - K12 PEACH PRODUCTS | Auckland | WEST K12 | 2024-09-15 | 45550.6937 | 2024-09-15 | 45550.7215 | 0.046774 | 0.0011693 | 732 | 29280 | Unplanned | Third party interference
1883 |  | 36039 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-09-16 | 45551.184 | 2024-09-16 | 45551.2319 | 0.093801 | 0.0032716 | 2048 | 58719 | Unplanned | Cause unknown
1884 |  | 36040 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-09-16 | 45551.2562 | 2024-09-16 | 45551.5951 | 0.04855 | 0.00025399 | 159 | 30392 | Unplanned | Third party interference
1885 |  | 36041 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-09-16 | 45551.2924 | 2024-09-16 | 45551.4694 | 0.074445 | 0.0011773 | 737 | 46602 | Unplanned | Wildlife
1886 |  | 36042 | BUSH K11 - K11 SCHNAPPER ROCK ROAD + LS | Northern | BUSH K11 | 2024-09-16 | 45551.2917 | 2024-09-16 | 45551.7319 | 0.0015783 | 8.3068e-05 | 26 | 988 | Planned | Planned
1887 |  | 36043 | WAIA K02 - K02 FIRTH ROAD | Northern | WAIA K02 | 2024-09-16 | 45551.366 | 2024-09-16 | 45551.7139 | 0.23166 | 0.0015016 | 940 | 145017 | Unplanned | Wildlife
1888 |  | 36044 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-16 | 45551.375 | 2024-09-16 | 45551.7215 | 0.094062 | 0.00018849 | 118 | 58882 | Planned | Planned
1889 |  | 36045 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-09-16 | 45551.4479 | 2024-09-16 | 45551.5236 | 0.0050496 | 4.6326e-05 | 29 | 3161 | Unplanned | Defective equipment
1890 |  | 36046 | SABU K02 - K02 HEPBURN RD | Northern | SABU K02 | 2024-09-16 | 45551.4563 | 2024-09-16 | 45551.4958 | 0.025924 | 0.001655 | 1036 | 16228 | Unplanned | Third party interference
1891 |  | 36047 | GINN K13 - K13 MELLING ST | Auckland | GINN K13 | 2024-09-16 | 45551.3458 | 2024-09-16 | 45551.4375 | 0.0075911 | 5.7509e-05 | 36 | 4752 | Unplanned | Cause unknown
1892 |  | 36048 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-16 | 45551.6215 | 2024-09-16 | 45551.625 | 0.00019968 | 3.9936e-05 | 25 | 125 | Unplanned | Other Cause | Outage caused by Tap Operation
1893 |  | 36049 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-16 | 45551.7125 | 2024-09-16 | 45551.816 | 0.024128 | 0.00040895 | 256 | 15104 | Unplanned | Cause unknown
1894 |  | 36050 | MNAB K33 - K33 GAVIN STREET EAST | Auckland | MNAB K33 | 2024-09-17 | 45552.0417 | 2024-09-17 | 45552.1667 | 0.049745 | 0.00027636 | 173 | 31140 | Planned | Planned
1895 |  | 36053 | BLMN K04 - K04 RANGATIRA | Northern | BLMN K04 | 2024-09-17 | 45552.3361 | 2024-09-17 | 45552.5521 | 0.012917 | 4.1534e-05 | 26 | 8086 | Planned | Planned
1896 |  | 36054 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-09-17 | 45552.3333 | 2024-09-17 | 45552.6979 | 0.045288 | 8.6263e-05 | 54 | 28350 | Planned | Planned
1897 |  | 36055 | WAIK K02 - K02 ROSIER ROAD | Northern | WAIK K02 | 2024-09-17 | 45552.3556 | 2024-09-17 | 45552.7396 | 0.54132 | 0.00098244 | 615 | 338865 | Planned | Planned
1898 |  | 36056 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-09-17 | 45552.3958 | 2024-09-17 | 45552.516 | 0.029571 | 0.00017093 | 107 | 18511 | Planned | Planned
1899 |  | 36059 | NSBT71 - TP SILVERDALE 2782 - KAUKAPAKAPA H01 (71) | Northern | KKAP K03 | 2024-09-17 | 45552.4861 | 2024-09-17 | 45552.9368 | 0.014138 | 0.00010862 | 68 | 8850 | Unplanned | Defective equipment
1900 |  | 36061 | BAIR K02 - K02 KERWYN AVE | Auckland | BAIR K02 | 2024-09-17 | 45552.5465 | 2024-09-17 | 45552.6861 | 0.00032109 | 1.597e-06 | 1 | 201 | Planned | Planned
1901 |  | 36062 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-09-17 | 45552.5437 | 2024-09-17 | 45552.6549 | 0.038083 | 0.00023801 | 149 | 23840 | Unplanned | Cause unknown
1902 |  | 36063 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-09-17 | 45552.5493 | 2024-09-17 | 45552.6882 | 0.3621 | 0.0052989 | 2050 | 226670 | Unplanned | Cause unknown
1903 |  | 36064 | TRIA K12 - K12 UNIVERSAL DRIVE | Northern | TRIA K12 | 2024-09-17 | 45552.5201 | 2024-09-17 | 45552.6611 | 0.037617 | 0.00018531 | 116 | 23548 | Unplanned | Defective equipment
1904 |  | 36075 | FORR K02 - K02 CASTOR BAY | Northern | FORR K02 | 2024-09-17 | 45552.6 | 2024-09-17 | 45552.6424 | 0.026019 | 0.0016997 | 1064 | 16288 | Unplanned | Vegetation
1905 |  | 36076 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-09-17 | 45552.5833 | 2024-09-17 | 45552.6521 | 0.14062 | 0.0018291 | 1145 | 88027 | Unplanned | Cause unknown
1906 |  | 36080 | DRIV K07 - K07 THE DRIVE | Auckland | DRIV K07 | 2024-09-17 | 45552.6097 | 2024-09-17 | 45552.6972 | 0.040055 | 0.00031789 | 199 | 25074 | Unplanned | Vegetation
1907 |  | 36081 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-09-17 | 45552.6403 | 2024-09-17 | 45552.7688 | 0.12036 | 0.0009345 | 585 | 75344 | Unplanned | Vegetation
1908 |  | 36082 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-17 | 45552.5437 | 2024-09-17 | 45552.7451 | 0.012045 | 4.1531e-05 | 26 | 7540 | Unplanned | Vegetation
1909 |  | 36083 | GULF K08 - K08 PINECREST DRIVE | Northern | GULF K08 | 2024-09-17 | 45552.5938 | 2024-09-18 | 45553.6368 | 0.0047988 | 3.195e-06 | 2 | 3004 | Unplanned | Vegetation
1910 |  | 36084 | BIRK K09 - K09 SALISBURY ROAD | Northern | BIRK K09 | 2024-09-17 | 45552.6951 | 2024-09-17 | 45552.8903 | 0.13152 | 0.00046806 | 293 | 82333 | Unplanned | Defective equipment
1911 |  | 36085 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-09-17 | 45552.491 | 2024-09-17 | 45552.7222 | 0.0063834 | 1.9169e-05 | 12 | 3996 | Unplanned | Defective equipment
1912 |  | 36087 | WAIK K02 - K02 ROSIER ROAD | Northern | WAIK K02 | 2024-09-17 | 45552.7396 | 2024-09-17 | 45552.8021 | 0.088419 | 0.00098244 | 615 | 55350 | Unplanned | Vegetation
1913 |  | 36088 | TAKA K16 - K16 BERWYN AVE | Auckland | MANU K12 | 2024-09-17 | 45552.8104 | 2024-09-18 | 45553.0931 | 0.14395 | 0.0016358 | 1024 | 90112 | Unplanned | Defective equipment
1914 |  | 36088 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-09-17 | 45552.8104 | 2024-09-18 | 45553.0931 | 0.44645 | 0.0029393 | 1840 | 279476 | Unplanned | Defective equipment
1915 |  | 36089 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-09-17 | 45552.7368 | 2024-09-17 | 45552.8549 | 0.003802 | 2.2364e-05 | 14 | 2380 | Unplanned | Vegetation
1916 |  | 36090 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-09-17 | 45552.8472 | 2024-09-18 | 45553.1687 | 0.1131 | 0.00046805 | 214 | 70800 | Unplanned | Defective equipment
1917 |  | 36091 | RBEA K11 - K11 TITAN PL | Northern | RBEA K11 | 2024-09-17 | 45552.7215 | 2024-09-17 | 45552.8743 | 0.0052716 | 2.3962e-05 | 15 | 3300 | Unplanned | Defective equipment
1918 |  | 36092 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-09-17 | 45552.7604 | 2024-09-17 | 45552.8854 | 0.0089138 | 4.9521e-05 | 31 | 5580 | Unplanned | Vegetation
1919 |  | 36093 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-09-17 | 45552.7007 | 2024-09-17 | 45552.9056 | 0.0028275 | 9.584e-06 | 6 | 1770 | Unplanned | Vegetation
1920 |  | 36094 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-17 | 45552.6271 | 2024-09-17 | 45552.9417 | 0.0014473 | 3.195e-06 | 2 | 906 | Unplanned | Vegetation
1921 |  | 36095 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-09-18 | 45553.084 | 2024-09-18 | 45553.0854 | 0.00079234 | 0.00039617 | 248 | 496 | Unplanned | Vegetation
1922 |  | 36097 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-18 | 45553.0924 | 2024-09-18 | 45553.7299 | 0.0029329 | 3.195e-06 | 2 | 1836 | Unplanned | Lightning
1923 |  | 36098 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-17 | 45552.684 | 2024-09-18 | 45553.0354 | 0.00080831 | 1.597e-06 | 1 | 506 | Unplanned | Vegetation
1924 |  | 36099 | BMON K03 - K03 CENTRAL | Northern | BMON K03 | 2024-09-18 | 45553.2917 | 2024-09-18 | 45553.6486 | 0.014578 | 0.00043132 | 135 | 9126 | Planned | Planned
1925 |  | 36100 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-18 | 45553.375 | 2024-09-18 | 45553.5715 | 0.018987 | 6.7091e-05 | 42 | 11886 | Planned | Planned
1926 |  | 36101 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-09-18 | 45553.3361 | 2024-09-18 | 45553.5785 | 0.064283 | 0.0001869 | 117 | 40241 | Planned | Planned
1927 |  | 36102 | TATA K11 - K11 YEOVIL ROAD | Northern | TATA K11 | 2024-09-18 | 45553.3597 | 2024-09-18 | 45553.7424 | 0.078859 | 0.00014537 | 91 | 49365 | Planned | Planned
1928 |  | 36103 | TORB K07 - K07 GLAMORGAN DRIVE | Northern | TORB K07 | 2024-09-18 | 45553.3368 | 2024-09-18 | 45553.7236 | 0.036481 | 6.5496e-05 | 41 | 22837 | Planned | Planned
1929 |  | 36104 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-09-18 | 45553.4403 | 2024-09-18 | 45553.5076 | 0.006663 | 6.8691e-05 | 43 | 4171 | Planned | Planned
1930 |  | 36105 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-09-17 | 45552.7424 | 2024-09-18 | 45553.566 | 0.12694 | 0.00010703 | 67 | 79462 | Unplanned | Defective equipment
1931 |  | 36106 | SIMP K08 - K08 SEIBEL ROAD | Northern | SIMP K08 | 2024-09-18 | 45553.5722 | 2024-09-18 | 45553.7708 | 0.025585 | 8.9458e-05 | 56 | 16016 | Unplanned | Defective equipment
1932 |  | 36107 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-09-17 | 45552.7778 | 2024-09-18 | 45553.3681 | 0.016294 | 1.9169e-05 | 12 | 10200 | Unplanned | Cause unknown
1933 |  | 36108 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-09-18 | 45553.7292 | 2024-09-18 | 45553.8403 | 0.0035783 | 2.2365e-05 | 14 | 2240 | Unplanned | Defective equipment
1934 |  | 36109 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-09-18 | 45553.3208 | 2024-09-18 | 45553.4306 | 0.0022716 | 1.4377e-05 | 9 | 1422 | Unplanned | Defective equipment
1935 |  | 36110 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-09-19 | 45554.1889 | 2024-09-19 | 45554.234 | 0.042593 | 0.00067094 | 420 | 26663 | Planned | Planned
1936 |  | 36122 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-09-17 | 45552.5889 | 2024-09-17 | 45552.6736 | 0.0029233 | 2.3961e-05 | 15 | 1830 | Unplanned | Vegetation
1937 |  | 36123 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-09-17 | 45552.5118 | 2024-09-17 | 45552.6597 | 0.00068052 | 3.195e-06 | 2 | 426 | Unplanned | Vegetation
1938 |  | 36124 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-09-17 | 45552.6681 | 2024-09-17 | 45552.7757 | 0.0096566 | 6.23e-05 | 39 | 6045 | Unplanned | Vegetation
1939 |  | 36125 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-09-18 | 45553.9319 | 2024-09-19 | 45554.0153 | 0.01189 | 0.00041215 | 258 | 7443 | Unplanned | Cause unknown
1940 |  | 36126 | GREE K19 - K19 TI RAKAU CENTRE | Auckland | GREE K19 | 2024-09-18 | 45553.9792 | 2024-09-19 | 45554.2076 | 0.024702 | 7.5081e-05 | 47 | 15463 | Planned | Planned
1941 |  | 36127 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-09-19 | 45554.3576 | 2024-09-19 | 45554.6292 | 0.058713 | 0.00015016 | 94 | 36754 | Planned | Planned
1942 |  | 36128 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-09-19 | 45554.3549 | 2024-09-19 | 45554.6076 | 0.043029 | 0.00011821 | 74 | 26936 | Planned | Planned
1943 |  | 36130 | RANU K09 - K09 ALIDADE PLACE | Northern | RANU K09 | 2024-09-19 | 45554.3646 | 2024-09-19 | 45554.7562 | 0.080186 | 0.00014217 | 89 | 50196 | Planned | Planned
1944 |  | 36131 | HPOI K07 - K07 POTTERY CRES | Northern | HPOI K07 | 2024-09-19 | 45554.3785 | 2024-09-19 | 45554.4424 | 0.004262 | 4.6326e-05 | 29 | 2668 | Unplanned | Vegetation
1945 |  | 36134 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-09-19 | 45554.5972 | 2024-09-19 | 45554.6882 | 0.0069058 | 5.2714e-05 | 33 | 4323 | Unplanned | Cause unknown
1946 |  | 36135 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2024-09-19 | 45554.6986 | 2024-09-19 | 45554.7486 | 0.018748 | 0.00026038 | 163 | 11736 | Unplanned | Vegetation
1947 |  | 36137 | MLEO K05 - K05 CARHAVEN | Northern | MLEO K05 | 2024-09-19 | 45554.875 | 2024-09-19 | 45554.9799 | 0.0038595 | 2.5559e-05 | 16 | 2416 | Planned | Planned
1948 |  | 36138 | GHIT K08 - K08 BERNARD MAGNUS LN | Northern | GHIT K08 | 2024-09-20 | 45555.2132 | 2024-09-20 | 45555.2597 | 0.028323 | 0.00097445 | 610 | 17730 | Unplanned | Lightning
1949 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.09892 | 0.00091696 | 379 | 61923 | Unplanned | Third party interference
1950 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM K02 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.0024345 | 0.00060862 | 381 | 1524 | Unplanned | Third party interference
1951 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM K03 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.0020448 | 0.00051118 | 320 | 1280 | Unplanned | Third party interference
1952 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM K05 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.0054378 | 0.0013594 | 851 | 3404 | Unplanned | Third party interference
1953 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM K06 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.0023579 | 0.00058945 | 369 | 1476 | Unplanned | Third party interference
1954 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM K08 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.004262 | 0.0010655 | 667 | 2668 | Unplanned | Third party interference
1955 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM K09 | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 0.013093 | 0.0032732 | 2049 | 8196 | Unplanned | Third party interference
1956 |  | 36141 | COAT K11 - K11 WAKE ROAD | Northern | WAIM LS | 2024-09-20 | 45555.2896 | 2024-09-20 | 45555.8111 | 6.39e-06 | 1.597e-06 | 1 | 4 | Unplanned | Third party interference
1957 |  | 36142 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-09-20 | 45555.3229 | 2024-09-20 | 45555.3368 | 0.0010224 | 5.1119e-05 | 32 | 640 | Unplanned | Lightning
1958 |  | 36143 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-09-20 | 45555.3993 | 2024-09-20 | 45555.5868 | 0.0025783 | 9.584e-06 | 6 | 1614 | Planned | Planned
1959 |  | 36144 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-09-20 | 45555.4271 | 2024-09-20 | 45555.4861 | 0.00013578 | 1.597e-06 | 1 | 85 | Planned | Planned
1960 |  | 36145 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-09-20 | 45555.2368 | 2024-09-20 | 45555.5042 | 0.0073803 | 1.9169e-05 | 12 | 4620 | Unplanned | Cause unknown
1961 |  | 36146 | WAIR K08 - K08 BOND CRESCENT | Northern | WAIR K08 | 2024-09-20 | 45555.6736 | 2024-09-20 | 45555.8229 | 0.016486 | 7.6678e-05 | 48 | 10320 | Unplanned | Defective equipment
1962 |  | 36147 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-09-20 | 45555.7799 | 2024-09-20 | 45555.7882 | 0.0021086 | 0.00017572 | 110 | 1320 | Unplanned | Third party interference
1963 |  | 36148 | REMU K07 - K07 GREENLANE RD EAST | Auckland | REMU K07 | 2024-09-20 | 45555.9285 | 2024-09-21 | 45556.3264 | 0.11076 | 0.00019329 | 121 | 69333 | Planned | Planned
1964 |  | 36149 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2024-09-21 | 45556.3333 | 2024-09-21 | 45556.6479 | 0.064405 | 0.00014217 | 89 | 40317 | Planned | Planned
1965 |  | 36150 | WOOD K06 - K06 POMARIA RD | Northern | WOOD K06 | 2024-09-21 | 45556.3597 | 2024-09-21 | 45556.6181 | 0.029118 | 7.8276e-05 | 49 | 18228 | Planned | Planned
1966 |  | 36151 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-09-21 | 45556.3958 | 2024-09-21 | 45556.5729 | 0.016701 | 6.5496e-05 | 41 | 10455 | Planned | Planned
1967 |  | 36152 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-21 | 45556.3035 | 2024-09-21 | 45556.3785 | 0.00017253 | 1.597e-06 | 1 | 108 | Unplanned | Wildlife
1968 |  | 36153 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-09-21 | 45556.3889 | 2024-09-21 | 45556.8299 | 0.059582 | 9.9042e-05 | 62 | 37298 | Planned | Planned
1969 |  | 36154 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-09-21 | 45556.4583 | 2024-09-21 | 45556.5604 | 0.081015 | 0.00055112 | 345 | 50715 | Planned | Planned
1970 |  | 36155 | WEST K09 - K09 TELSTRA SATURN | Auckland | WEST K09 | 2024-09-21 | 45556.4167 | 2024-09-21 | 45556.6319 | 0.0099042 | 3.1949e-05 | 20 | 6200 | Planned | Planned
1971 |  | 36156 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-22 | 45557.3542 | 2024-09-22 | 45557.7507 | 0.012476 | 2.2364e-05 | 14 | 7810 | Planned | Planned
1972 |  | 36158 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-09-22 | 45557.6396 | 2024-09-22 | 45557.6875 | 0.00011022 | 1.597e-06 | 1 | 69 | Unplanned | Cause unknown
1973 |  | 36159 | PAKU K13 - K13 THE BOULEVARD | Auckland | PAKU K13 | 2024-09-22 | 45557.7188 | 2024-09-22 | 45557.8889 | 0.045889 | 0.00072525 | 227 | 28726 | Unplanned | Defective equipment
1974 |  | 36160 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-09-22 | 45557.8354 | 2024-09-23 | 45558.2174 | 0.080831 | 0.00014696 | 92 | 50600 | Planned | Planned
1975 |  | 36161 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-09-22 | 45557.9146 | 2024-09-23 | 45558.0146 | 0.016837 | 0.0019537 | 1223 | 10540 | Unplanned | Cause unknown
1976 |  | 36162 | PARN K11 - K11 BONNICI MOTORS VIA SW/STN | Auckland | PARN K11 | 2024-09-23 | 45558.1049 | 2024-09-23 | 45558.2292 | 0.034679 | 0.00021566 | 127 | 21709 | Unplanned | Defective equipment
1977 |  | 36163 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-09-23 | 45558.2472 | 2024-09-23 | 45558.3299 | 0.0022812 | 1.917e-05 | 12 | 1428 | Unplanned | Wildlife
1978 |  | 36164 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-09-23 | 45558.3764 | 2024-09-23 | 45558.4688 | 0.00084985 | 6.39e-06 | 4 | 532 | Planned | Planned
1979 |  | 36165 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-09-23 | 45558.3847 | 2024-09-23 | 45558.5826 | 0.029138 | 0.00010224 | 64 | 18240 | Planned | Planned
1980 |  | 36167 | LIVE K18 - K18 QUEEN CITY APARTMENTS | Auckland | LIVE K18 | 2024-09-23 | 45558.9174 | 2024-09-24 | 45559.1931 | 0.11289 | 0.00028435 | 178 | 70666 | Planned | Planned
1981 |  | 36168 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-09-24 | 45559.0125 | 2024-09-24 | 45559.1493 | 0.028026 | 0.00025239 | 158 | 17544 | Unplanned | Cause unknown
1982 |  | 36169 | FREE K13 - K13 WILKINS ST (5) | Auckland | FREE K56 | 2024-09-24 | 45559.0278 | 2024-09-24 | 45559.2007 | 0.00039777 | 1.597e-06 | 1 | 249 | Planned | Planned
1983 |  | 36170 | FBSH K05 - K05 WISTERIA LANE | Auckland | FBSH K05 | 2024-09-24 | 45559.1028 | 2024-09-24 | 45559.7868 | 0.47044 | 0.0051326 | 3158 | 294492 | Unplanned | Third party interference
1984 |  | 36171 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-24 | 45559.3556 | 2024-09-24 | 45559.741 | 0.04167 | 7.5079e-05 | 47 | 26085 | Planned | Planned
1985 |  | 36172 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-09-24 | 45559.3826 | 2024-09-24 | 45559.4271 | 0.022705 | 0.0032876 | 2058 | 14213 | Unplanned | Defective equipment
1986 |  | 36173 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-09-24 | 45559.366 | 2024-09-24 | 45559.5507 | 0.03017 | 0.00011341 | 71 | 18886 | Planned | Planned
1987 |  | 36174 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-09-24 | 45559.3333 | 2024-09-24 | 45559.6667 | 0.0061342 | 1.2776e-05 | 8 | 3840 | Planned | Planned
1988 |  | 36175 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-09-24 | 45559.3562 | 2024-09-24 | 45559.7076 | 0.36455 | 0.00072046 | 451 | 228206 | Planned | Planned
1989 |  | 36176 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-09-24 | 45559.4375 | 2024-09-24 | 45559.6646 | 0.10134 | 0.0003099 | 194 | 63438 | Planned | Planned
1990 |  | 36177 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-09-24 | 45559.4347 | 2024-09-24 | 45559.4375 | 0.00026198 | 6.5496e-05 | 41 | 164 | Unplanned | Other Cause | Outage caused by Tap Operation
1991 |  | 36178 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2024-09-24 | 45559.5278 | 2024-09-24 | 45559.6208 | 0.030511 | 0.00034984 | 219 | 19100 | Unplanned | Vegetation
1992 |  | 36179 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-09-24 | 45559.5799 | 2024-09-24 | 45559.591 | 0.0016358 | 0.00010224 | 64 | 1024 | Unplanned | Vegetation
1993 |  | 36180 | SHEL K09 - K09 BARDSEY ST | Auckland | SHEL K09 | 2024-09-24 | 45559.375 | 2024-09-24 | 45559.6625 | 0.23875 | 0.00057668 | 361 | 149454 | Planned | Planned
1994 |  | 36181 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-09-24 | 45559.7653 | 2024-09-24 | 45559.8333 | 0.00015655 | 1.597e-06 | 1 | 98 | Unplanned | Cause unknown
1995 |  | 36182 | BRIC K10 - K10 ASTLEY AVE | Northern | BRIC K10 | 2024-09-25 | 45560.0208 | 2024-09-25 | 45560.0611 | 0.0044473 | 7.6678e-05 | 48 | 2784 | Unplanned | Third party interference
1996 |  | 36183 | DRIV K04 - K04 PARKLANE MOTEL | Auckland | DRIV K04 | 2024-09-24 | 45559.8632 | 2024-09-27 | 45562.5833 | 0.0062572 | 1.597e-06 | 1 | 3917 | Unplanned | Defective equipment
1997 |  | 36184 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-25 | 45560.375 | 2024-09-25 | 45560.6715 | 0.055933 | 0.00013099 | 82 | 35014 | Planned | Planned
1998 |  | 36185 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-09-25 | 45560.3979 | 2024-09-25 | 45560.5306 | 0.031732 | 0.00016613 | 104 | 19864 | Planned | Planned
1999 |  | 36186 | SIMP K08 - K08 SEIBEL ROAD | Northern | SIMP K08 | 2024-09-25 | 45560.2326 | 2024-09-25 | 45560.3125 | 0.0022045 | 1.9169e-05 | 12 | 1380 | Unplanned | Cause unknown
2000 |  | 36187 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-09-25 | 45560.3007 | 2024-09-25 | 45560.6972 | 0.20378 | 0.00036582 | 229 | 127563 | Planned | Planned
2001 |  | 36188 | TAKA K13 - K13 COSGROVE RD | Auckland | TAKA K13 | 2024-09-25 | 45560.3958 | 2024-09-25 | 45560.6181 | 0.077189 | 0.00024122 | 151 | 48320 | Planned | Planned
2002 |  | 36189 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-09-25 | 45560.4375 | 2024-09-25 | 45560.4792 | 0.0001917 | 3.195e-06 | 2 | 120 | Unplanned | Defective equipment
2003 |  | 36190 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-09-25 | 45560.6007 | 2024-09-25 | 45560.6771 | 0.00035144 | 3.195e-06 | 2 | 220 | Unplanned | Defective equipment
2004 |  | 36191 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2024-09-25 | 45560.8215 | 2024-09-26 | 45561.1285 | 0.071331 | 0.0002172 | 136 | 44653 | Unplanned | Defective equipment
2005 |  | 36191 | WELL K03 - K03 WAYBY | Northern | WELL K09 | 2024-09-25 | 45560.8215 | 2024-09-26 | 45561.1285 | 0.0020576 | 0.0010287 | 644 | 1288 | Unplanned | Defective equipment
2006 |  | 36192 | TRIA K02 - K02 SOUTH | Northern | TRIA K02 | 2024-09-25 | 45560.9167 | 2024-09-26 | 45561.1472 | 0.15646 | 0.00047125 | 295 | 97940 | Planned | Planned
2007 |  | 36193 | HPOI K12 - K12 HOBSONVILLE RD | Northern | HPOI K12 | 2024-09-25 | 45560.9167 | 2024-09-26 | 45561.2083 | 0.0040256 | 9.585e-06 | 6 | 2520 | Planned | Planned
2008 |  | 36194 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-09-26 | 45561.3431 | 2024-09-26 | 45561.6882 | 0.17037 | 0.00034667 | 217 | 106650 | Planned | Planned
2009 |  | 36195 | SNEL K08 - K08 ALGIES BAY | Northern | SNEL K08 | 2024-09-26 | 45561.3576 | 2024-09-26 | 45561.691 | 0.14722 | 0.00030671 | 192 | 92160 | Planned | Planned
2010 |  | 36196 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-09-26 | 45561.2889 | 2024-09-26 | 45561.3854 | 0.00022205 | 1.597e-06 | 1 | 139 | Unplanned | Wildlife
2011 |  | 36198 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-09-26 | 45561.2722 | 2024-09-26 | 45561.3333 | 0.00014058 | 1.597e-06 | 1 | 88 | Unplanned | Cause unknown
2012 |  | 36200 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-09-26 | 45561.7896 | 2024-09-26 | 45561.941 | 0.010447 | 4.7921e-05 | 30 | 6540 | Unplanned | Defective equipment
2013 |  | 36201 | RBEA K02 - K02 FANTAIL COURT + LS | Northern | RBEA K02 | 2024-09-26 | 45561.875 | 2024-09-27 | 45562.2167 | 0.21861 | 0.00050959 | 319 | 136851 | Planned | Planned
2014 |  | 36201 | RBEA K02 - K02 FANTAIL COURT + LS | Northern | RBEA K03 | 2024-09-26 | 45561.875 | 2024-09-27 | 45562.2167 | 0.30006 | 0.00065975 | 413 | 187838 | Planned | Planned
2015 |  | 36202 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-09-26 | 45561.875 | 2024-09-26 | 45561.9986 | 0.0005687 | 3.195e-06 | 2 | 356 | Planned | Planned
2016 |  | 36203 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-09-26 | 45561.7847 | 2024-09-26 | 45561.9667 | 0.00083707 | 3.195e-06 | 2 | 524 | Unplanned | Wildlife
2017 |  | 36204 | LIVE K18 - K18 QUEEN CITY APARTMENTS | Auckland | LIVE K18 | 2024-09-27 | 45562.2181 | 2024-09-27 | 45562.2979 | 0.099364 | 0.0012252 | 767 | 62201 | Unplanned | Defective equipment
2018 |  | 36205 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-09-27 | 45562.3333 | 2024-09-27 | 45562.6819 | 0.11147 | 0.00022204 | 139 | 69778 | Planned | Planned
2019 |  | 36206 | OREW K05 - K05 CENTREWAY | Northern | OREW K05 | 2024-09-27 | 45562.3333 | 2024-09-27 | 45562.5806 | 0.011943 | 3.3547e-05 | 21 | 7476 | Planned | Planned
2020 |  | 36207 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-09-27 | 45562.3347 | 2024-09-27 | 45562.6257 | 0.046184 | 0.00011022 | 69 | 28911 | Planned | Planned
2021 |  | 36208 | NLYN K08 - K08 TOTARA AVENUE | Northern | NLYN K08 | 2024-09-27 | 45562.3611 | 2024-09-27 | 45562.4028 | 0 | 0 | 0 | 0 | Unplanned | Third party interference
2022 |  | 36209 | WIRI K02 - K02 KENDERDINE RD | Auckland | WIRI K02 | 2024-09-27 | 45562.5556 | 2024-09-27 | 45562.6208 | 0.036077 | 0.00049681 | 311 | 22584 | Unplanned | Cause unknown
2023 |  | 36210 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-09-27 | 45562.6333 | 2024-09-27 | 45562.7681 | 0.0021694 | 1.1182e-05 | 7 | 1358 | Unplanned | Defective equipment
2024 |  | 36211 | RIVE K10 - K10 HUAPAI | Northern | RIVE K10 | 2024-09-28 | 45563.3347 | 2024-09-28 | 45563.7194 | 0.10797 | 0.00019489 | 122 | 67588 | Planned | Planned
2025 |  | 36211 | RIVE K10 - K10 HUAPAI | Northern | RIVE K11 | 2024-09-28 | 45563.3347 | 2024-09-28 | 45563.7194 | 0.046905 | 8.4664e-05 | 53 | 29362 | Planned | Planned
2026 |  | 36212 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2024-09-27 | 45562.9757 | 2024-09-28 | 45563.1306 | 0.066972 | 0.00030032 | 188 | 41924 | Unplanned | Defective equipment
2027 |  | 36213 | NEWT K22 - K22 HOHIPERE ST | Auckland | NEWT K22 | 2024-09-28 | 45563.0569 | 2024-09-28 | 45563.1583 | 0.16787 | 0.0015847 | 992 | 105084 | Unplanned | Defective equipment
2028 |  | 36214 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-09-28 | 45563.4688 | 2024-09-28 | 45563.6076 | 0.0067093 | 3.3544e-05 | 21 | 4200 | Unplanned | Defective equipment
2029 |  | 36215 | MALB K16 - K16 WILCOTT ST | Auckland | MALB K16 | 2024-09-28 | 45563.7104 | 2024-09-28 | 45563.7479 | 0.010438 | 0.00019329 | 121 | 6534 | Unplanned | Defective equipment
2030 |  | 36216 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-09-28 | 45563.8611 | 2024-09-28 | 45563.9729 | 0.20132 | 0.0016374 | 1025 | 126025 | Unplanned | Defective equipment
2031 |  | 36217 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-09-28 | 45563.9167 | 2024-09-29 | 45564.0486 | 0.090574 | 0.00062621 | 392 | 56699 | Planned | Planned
2032 |  | 36219 | KEEL K13 - K13 SWANSON ROAD | Northern | KEEL K13 | 2024-09-29 | 45564.375 | 2024-09-29 | 45564.7882 | 0.001901 | 3.195e-06 | 2 | 1190 | Planned | Planned
2033 |  | 36220 | KKAP K06 - K06 PEAK RD | Northern | KKAP K06 | 2024-09-29 | 45564.4021 | 2024-09-29 | 45564.6715 | 0.001778 | 4.794e-06 | 3 | 1113 | Planned | Planned
2034 |  | 36221 | TRIA K04 - K04 WAIMUMU RD | Northern | TRIA K04 | 2024-09-29 | 45564.4563 | 2024-09-29 | 45564.9271 | 0.14143 | 0.0015591 | 513 | 88534 | Unplanned | Third party interference
2035 |  | 36222 | MLEO K05 - K05 CARHAVEN | Northern | MLEO K05 | 2024-09-29 | 45564.6521 | 2024-09-29 | 45564.6847 | 0.056438 | 0.0015927 | 997 | 35330 | Unplanned | Cause unknown
2036 |  | 36223 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-09-29 | 45564.9792 | 2024-09-30 | 45565.0764 | 0.0040256 | 2.8754e-05 | 18 | 2520 | Planned | Planned
2037 |  | 36224 | HOWI K10 - K10 FINNERTY AVE | Auckland | HOWI K10 | 2024-09-30 | 45565.4021 | 2024-09-30 | 45565.6083 | 0.025146 | 8.4665e-05 | 53 | 15741 | Planned | Planned
2038 |  | 36225 | DRIV K04 - K04 PARKLANE MOTEL | Auckland | DRIV K04 | 2024-09-30 | 45565.375 | 2024-09-30 | 45565.4271 | 0.00011981 | 1.597e-06 | 1 | 75 | Planned | Planned
2039 |  | 36226 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-09-30 | 45565.5674 | 2024-09-30 | 45565.625 | 0.00013259 | 1.597e-06 | 1 | 83 | Unplanned | Other Cause | Outage caused by Tap Operation
2040 |  | 36227 | ROCK K15 - K15 MAROA RD | Auckland | ROCK K15 | 2024-09-30 | 45565.7535 | 2024-10-01 | 45566.0347 | 0.0047125 | 0.000377 | 118 | 2950 | Unplanned | Other Cause | Outage caused by Tap Operation
2041 |  | 36228 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K05 | 2024-09-30 | 45565.9792 | 2024-10-01 | 45566.1431 | 0.045994 | 0.00019489 | 122 | 28792 | Planned | Planned
2042 |  | 36228 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K13 | 2024-09-30 | 45565.9792 | 2024-10-01 | 45566.1431 | 0.18096 | 0.00076678 | 480 | 113280 | Planned | Planned
2043 |  | 36229 | NLYN K11 - K11 GARDENER ROAD | Northern | NLYN K11 | 2024-10-01 | 45566.3333 | 2024-10-01 | 45566.5986 | 0.075482 | 0.0006278 | 313 | 47251 | Planned | Planned
2044 |  | 36230 | MKIN K11 - K11 THE AVENUE | Northern | MKIN K11 | 2024-10-01 | 45566.3368 | 2024-10-01 | 45566.6993 | 0.032521 | 6.2301e-05 | 39 | 20358 | Planned | Planned
2045 |  | 36231 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2024-10-01 | 45566.3368 | 2024-10-01 | 45566.7139 | 0.0086742 | 1.5975e-05 | 10 | 5430 | Planned | Planned
2046 |  | 36232 | PAKU K04 - K04 REEVES RD | Auckland | PAKU K04 | 2024-10-01 | 45566.3958 | 2024-10-01 | 45566.6354 | 0.20722 | 0.00060064 | 376 | 129720 | Planned | Planned
2047 |  | 36233 | BAIR K14 - K14 WYMONDLEY | Auckland | BAIR K14 | 2024-10-01 | 45566.3965 | 2024-10-01 | 45566.6319 | 0.063902 | 0.0001885 | 118 | 40002 | Planned | Planned
2048 |  | 36234 | WAIK K02 - K02 ROSIER ROAD | Northern | WAIK K02 | 2024-10-01 | 45566.5417 | 2024-10-01 | 45566.6562 | 0.068267 | 0.00041374 | 259 | 42735 | Planned | Planned
2049 |  | 36235 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-10-01 | 45566.5667 | 2024-10-02 | 45567.1736 | 0.072464 | 0.00046804 | 213 | 45362 | Unplanned | Third party interference
2050 |  | 36236 | MCEN K05 - K05 BADER DRIVE | Auckland | MCEN K05 | 2024-10-01 | 45566.6042 | 2024-10-01 | 45566.7757 | 0.014599 | 5.9106e-05 | 37 | 9139 | Unplanned | Defective equipment
2051 |  | 36238 | NEWT K22 - K22 HOHIPERE ST | Auckland | NEWT K22 | 2024-10-01 | 45566.9174 | 2024-10-02 | 45567.1813 | 0.018818 | 4.9521e-05 | 31 | 11780 | Planned | Planned
2052 |  | 36239 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | AVON K03 | 2024-10-01 | 45566.9792 | 2024-10-02 | 45567.1361 | 0.21301 | 0.0009425 | 590 | 133340 | Planned | Planned
2053 |  | 36240 | HPOI K12 - K12 HOBSONVILLE RD | Northern | HPOI K12 | 2024-10-02 | 45567.2118 | 2024-10-02 | 45567.2125 | 2.0766e-05 | 2.0766e-05 | 13 | 13 | Planned | Planned
2054 |  | 36242 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-10-02 | 45567.3958 | 2024-10-02 | 45567.7222 | 0.15467 | 0.00032908 | 206 | 96820 | Planned | Planned
2055 |  | 36243 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2024-10-02 | 45567.3542 | 2024-10-02 | 45567.7486 | 0.20609 | 0.00037061 | 232 | 129008 | Planned | Planned
2056 |  | 36244 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-10-02 | 45567.3549 | 2024-10-02 | 45567.7049 | 0.0056358 | 1.1182e-05 | 7 | 3528 | Planned | Planned
2057 |  | 36245 | BROW K05 - K05 ARRAN ROAD & LS | Northern | BROW K05 | 2024-10-02 | 45567.375 | 2024-10-02 | 45567.5674 | 0.093496 | 0.00035783 | 224 | 58528 | Planned | Planned
2058 |  | 36246 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-10-02 | 45567.6396 | 2024-10-02 | 45567.9236 | 0.056186 | 0.0020207 | 1226 | 35172 | Unplanned | Defective equipment
2059 |  | 36247 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-10-02 | 45567.7382 | 2024-10-03 | 45568.4785 | 0.12711 | 0.0014201 | 889 | 79569 | Unplanned | Third party interference
2060 |  | 36248 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-10-02 | 45567.8708 | 2024-10-02 | 45567.9979 | 0.11124 | 0.0012332 | 772 | 69636 | Unplanned | Vegetation
2061 |  | 36249 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-10-02 | 45567.9792 | 2024-10-03 | 45568.1264 | 0.083649 | 0.00039457 | 247 | 52364 | Planned | Planned
2062 |  | 36252 | BMON K08 - K08 CHELTENHAM | Northern | BMON K08 | 2024-10-02 | 45567.9618 | 2024-10-03 | 45568.2257 | 0.16118 | 0.0016965 | 1062 | 100900 | Unplanned | Defective equipment
2063 |  | 36253 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-10-02 | 45567.9639 | 2024-10-03 | 45568.1 | 0.12086 | 0.00061661 | 386 | 75656 | Unplanned | Vegetation
2064 |  | 36254 | LAIN K08 - K08 HUIA PUMPS | Northern | LAIN K08 | 2024-10-02 | 45567.9896 | 2024-10-03 | 45568.0701 | 0.00092333 | 7.989e-06 | 5 | 578 | Unplanned | Cause unknown
2065 |  | 36255 | NEWM K02 - K02 BROADWAY CENTRE | Auckland | NEWM K02 | 2024-10-03 | 45568.0431 | 2024-10-03 | 45568.1229 | 0.012125 | 0.00010543 | 66 | 7590 | Unplanned | Vegetation
2066 |  | 36256 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-10-03 | 45568.0431 | 2024-10-03 | 45568.2917 | 0.1268 | 0.0021518 | 1347 | 79373 | Unplanned | Vegetation
2067 |  | 36257 | BROW K11 - K11 SARTORS AVE | Northern | BROW K11 | 2024-10-02 | 45567.9 | 2024-10-03 | 45568.1 | 0.033125 | 0.00011502 | 72 | 20736 | Unplanned | Vegetation
2068 |  | 36258 | LAIN K08 - K08 HUIA PUMPS | Northern | LAIN K03 | 2024-10-03 | 45568.3139 | 2024-10-03 | 45568.4146 | 0.011645 | 0.00077636 | 486 | 7290 | Unplanned | Vegetation
2069 |  | 36258 | LAIN K08 - K08 HUIA PUMPS | Northern | LAIN K08 | 2024-10-03 | 45568.3139 | 2024-10-03 | 45568.4146 | 0.0011582 | 7.99e-06 | 5 | 725 | Unplanned | Vegetation
2070 |  | 36259 | ECOA K02 - K02 SUNRISE AVENUE | Northern | ECOA K02 | 2024-10-03 | 45568.3333 | 2024-10-03 | 45568.7188 | 0.22697 | 0.00040895 | 256 | 142080 | Planned | Planned
2071 |  | 36260 | BIRK K09 - K09 SALISBURY ROAD | Northern | BIRK K09 | 2024-10-03 | 45568.3542 | 2024-10-03 | 45568.809 | 0.14752 | 0.00022524 | 141 | 92345 | Planned | Planned
2072 |  | 36261 | HOWI K13 - K13 MALVINA PL | Auckland | HOWI K13 | 2024-10-03 | 45568.4132 | 2024-10-03 | 45568.7431 | 0.066015 | 0.00013898 | 87 | 41325 | Planned | Planned
2073 |  | 36262 | ORAK K11 - K11 KOHIMARAMA RD | Auckland | ORAK K11 | 2024-10-03 | 45568.4354 | 2024-10-03 | 45568.7937 | 0.15084 | 0.00029234 | 183 | 94428 | Planned | Planned
2074 |  | 36263 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-03 | 45568.4201 | 2024-10-03 | 45568.5007 | 0.0022237 | 1.917e-05 | 12 | 1392 | Planned | Planned
2075 |  | 36264 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-10-03 | 45568.4257 | 2024-10-03 | 45568.5076 | 0.12271 | 0.0010399 | 651 | 76818 | Planned | Planned
2076 |  | 36265 | DRIV K05 - K05 ONSLOW AVE | Auckland | DRIV K05 | 2024-10-03 | 45568.584 | 2024-10-03 | 45568.65 | 0.052508 | 0.00055272 | 346 | 32870 | Unplanned | Defective equipment
2077 |  | 36266 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-10-03 | 45568.1958 | 2024-10-03 | 45568.5312 | 0.0030863 | 6.39e-06 | 4 | 1932 | Unplanned | Cause unknown
2078 |  | 36267 | ROCK K17 - K17 ORANGA AVE | Auckland | ROCK K17 | 2024-10-03 | 45568.2528 | 2024-10-03 | 45568.3958 | 0.026984 | 0.00013099 | 82 | 16892 | Unplanned | Cause unknown
2079 |  | 36268 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-03 | 45568.7049 | 2024-10-03 | 45568.7903 | 0.014737 | 0.00011981 | 75 | 9225 | Unplanned | Defective equipment
2080 |  | 36269 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-10-03 | 45568.7431 | 2024-10-03 | 45568.9083 | 0.001901 | 7.987e-06 | 5 | 1190 | Unplanned | Vegetation
2081 |  | 36270 | TRIA K02 - K02 SOUTH | Northern | TRIA K02 | 2024-10-03 | 45568.7465 | 2024-10-03 | 45568.8889 | 0.0016374 | 7.987e-06 | 5 | 1025 | Unplanned | Defective equipment
2082 |  | 36271 | PARN K12 - K12 RUSKIN ST (NOVA) | Auckland | PARN K12 | 2024-10-03 | 45568.9792 | 2024-10-04 | 45569.1174 | 0.079791 | 0.00040096 | 251 | 49949 | Planned | Planned
2083 |  | 36272 | JAME K01 - K01 WELDENE | Northern | JAME K01 | 2024-10-03 | 45568.875 | 2024-10-03 | 45568.9965 | 0.0058707 | 3.3547e-05 | 21 | 3675 | Planned | Planned
2084 |  | 36273 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-10-03 | 45568.941 | 2024-10-04 | 45569.3729 | 0.0511 | 0.00010703 | 67 | 31988 | Unplanned | Defective equipment
2085 |  | 36274 | KING K12 - K12 GT NORTH RD | Auckland | KING K12 | 2024-10-04 | 45569.0826 | 2024-10-04 | 45569.2097 | 0.19136 | 0.0012844 | 804 | 119793 | Unplanned | Defective equipment
2086 |  | 36276 | RIVE K04 - K04 BARRETT RD | Northern | RIVE K04 | 2024-10-04 | 45569.3542 | 2024-10-04 | 45569.7458 | 0.16398 | 0.00029073 | 182 | 102648 | Planned | Planned
2087 |  | 36277 | AVON K06 - K06 NEW NORTH RD. 1225 | Auckland | AVON K06 | 2024-10-04 | 45569.4167 | 2024-10-04 | 45569.75 | 0.16486 | 0.00034345 | 215 | 103200 | Planned | Planned
2088 |  | 36279 | SJOH K09 - K09 168 NORMAN LESSER DR | Auckland | SJOH K09 | 2024-10-05 | 45570.0028 | 2024-10-05 | 45570.1979 | 0.017321 | 8.9458e-05 | 56 | 10843 | Unplanned | Defective equipment
2089 |  | 36280 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-10-05 | 45570.1083 | 2024-10-05 | 45570.1424 | 0.0051662 | 0.00010543 | 66 | 3234 | Unplanned | Defective equipment
2090 |  | 36282 | WIRI K02 - K02 KENDERDINE RD | Auckland | WIRI K02 | 2024-10-05 | 45570.3854 | 2024-10-05 | 45570.3924 | 1.5975e-05 | 1.597e-06 | 1 | 10 | Planned | Planned
2091 |  | 36283 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-10-05 | 45570.6361 | 2024-10-05 | 45570.7347 | 0.00045368 | 3.195e-06 | 2 | 284 | Unplanned | Cause unknown
2092 |  | 36284 | BALM K02 - K02 ARABI STREET | Auckland | BALM K02 | 2024-10-05 | 45570.9021 | 2024-10-06 | 45571.0271 | 0.091439 | 0.00050799 | 318 | 57240 | Unplanned | Third party interference
2093 |  | 36285 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-10-06 | 45571.3542 | 2024-10-06 | 45571.459 | 0.0021709 | 1.4377e-05 | 9 | 1359 | Unplanned | Wildlife
2094 |  | 36286 | BAIR K04 - K04 ASHTON AVENUE | Auckland | BAIR K04 | 2024-10-06 | 45571.6806 | 2024-10-06 | 45571.7097 | 0.037151 | 0.0023131 | 1448 | 23256 | Unplanned | Vegetation
2095 |  | 36287 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-10-06 | 45571.809 | 2024-10-07 | 45572.1569 | 0.028748 | 0.00021726 | 136 | 17996 | Unplanned | Third party interference
2096 |  | 36288 | BMON K08 - K08 CHELTENHAM | Northern | BMON K08 | 2024-10-06 | 45571.875 | 2024-10-06 | 45571.959 | 0.0038659 | 3.1949e-05 | 20 | 2420 | Planned | Planned
2097 |  | 36289 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | MKAU K19 | 2024-10-06 | 45571.8771 | 2024-10-06 | 45571.9215 | 0.034448 | 0.0015432 | 966 | 21564 | Unplanned | Cause unknown
2098 |  | 36291 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-07 | 45572.2819 | 2024-10-07 | 45572.3014 | 0.014 | 0.0005 | 313 | 8764 | Unplanned | Cause unknown
2099 |  | 36292 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-10-07 | 45572.2833 | 2024-10-07 | 45572.4146 | 0.13375 | 0.0013898 | 826 | 83726 | Unplanned | Cause unknown
2100 |  | 36293 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-10-07 | 45572.3625 | 2024-10-07 | 45572.7153 | 0.012577 | 2.556e-05 | 16 | 7873 | Planned | Planned
2101 |  | 36294 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-10-07 | 45572.4208 | 2024-10-07 | 45572.6535 | 0.25308 | 0.0029425 | 1842 | 158427 | Unplanned | Defective equipment
2102 |  | 36296 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-10-07 | 45572.5306 | 2024-10-07 | 45572.8194 | 0.0013291 | 3.195e-06 | 2 | 832 | Unplanned | Vegetation
2103 |  | 36297 | JAME K10 - K10 HOGANS ROAD | Northern | JAME K10 | 2024-10-07 | 45572.7201 | 2024-10-08 | 45573.0007 | 0.024202 | 0.00043451 | 272 | 15150 | Unplanned | Defective equipment
2104 |  | 36301 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-10-07 | 45572.7438 | 2024-10-07 | 45572.8229 | 0.00018211 | 1.597e-06 | 1 | 114 | Unplanned | Vegetation
2105 |  | 36302 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2024-10-08 | 45573.4042 | 2024-10-08 | 45573.6715 | 0.17651 | 0.00045847 | 287 | 110495 | Planned | Planned
2106 |  | 36303 | MNAB K03 - K03 LEONARD RD | Auckland | MNAB K03 | 2024-10-08 | 45573.3958 | 2024-10-08 | 45573.4542 | 0.025227 | 0.00030032 | 188 | 15792 | Planned | Planned
2107 |  | 36304 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-10-08 | 45573.4201 | 2024-10-08 | 45573.659 | 0.047809 | 0.00013898 | 87 | 29928 | Planned | Planned
2108 |  | 36305 | ATKI K09 - K09 KAURILANDS RD | Northern | ATKI K09 | 2024-10-08 | 45573.3924 | 2024-10-08 | 45573.4299 | 0.081927 | 0.0024425 | 1529 | 51286 | Unplanned | Cause unknown
2109 |  | 36306 | ECOA K07 - K07 OAKTREE AVENUE | Northern | ECOA K07 | 2024-10-08 | 45573.3542 | 2024-10-08 | 45573.7 | 0.13683 | 0.00027476 | 172 | 85656 | Planned | Planned
2110 |  | 36307 | TATA K02 - K02 TAIKATA RD | Northern | TATA K02 | 2024-10-08 | 45573.4014 | 2024-10-08 | 45573.6333 | 0.078966 | 0.00023642 | 148 | 49432 | Planned | Planned
2111 |  | 36308 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-08 | 45573.3611 | 2024-10-08 | 45573.6104 | 0.00057349 | 1.597e-06 | 1 | 359 | Planned | Planned
2112 |  | 36309 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-10-08 | 45573.3993 | 2024-10-08 | 45573.6368 | 0.034965 | 0.00010224 | 64 | 21888 | Planned | Planned
2113 |  | 36310 | ECOA K07 - K07 OAKTREE AVENUE | Northern | BROW K03 | 2024-10-08 | 45573.7125 | 2024-10-08 | 45573.775 | 0.049873 | 0.00071247 | 446 | 31220 | Unplanned | Human error
2114 |  | 36310 | ECOA K07 - K07 OAKTREE AVENUE | Northern | ECOA K07 | 2024-10-08 | 45573.7125 | 2024-10-08 | 45573.775 | 0.0063004 | 0.00018531 | 116 | 3944 | Unplanned | Human error
2115 |  | 36311 | WAIR K06 - K06 DIANA DRIVE | Northern | WAIR K06 | 2024-10-08 | 45573.9167 | 2024-10-09 | 45574.0285 | 0.0020575 | 1.278e-05 | 8 | 1288 | Planned | Planned
2116 |  | 36313 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-10-09 | 45574.0569 | 2024-10-09 | 45574.2396 | 0.046023 | 0.00091699 | 553 | 28810 | Unplanned | Wildlife
2117 |  | 36314 | TRIA K03 - K03 COLWILL RD | Northern | TRIA K03 | 2024-10-09 | 45574.0743 | 2024-10-09 | 45574.2368 | 0.083413 | 0.0008211 | 514 | 52216 | Unplanned | Cause unknown
2118 |  | 36316 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-10-09 | 45574.1542 | 2024-10-09 | 45574.6424 | 0.1066 | 0.00023642 | 148 | 66729 | Unplanned | Defective equipment
2119 |  | 36317 | KEEL K06 - K06 HICKORY AVE | Northern | KEEL K06 | 2024-10-09 | 45574.25 | 2024-10-09 | 45574.7743 | 0.18428 | 0.0012316 | 434 | 115360 | Planned | Planned
2120 |  | 36318 | WAIA K01 - K01 MIZPAH ROAD | Northern | WAIA K01 | 2024-10-09 | 45574.3333 | 2024-10-09 | 45574.7465 | 0.023762 | 3.9936e-05 | 25 | 14875 | Planned | Planned
2121 |  | 36319 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-10-09 | 45574.3562 | 2024-10-09 | 45574.6965 | 0.00078275 | 1.598e-06 | 1 | 490 | Planned | Planned
2122 |  | 36320 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-10-09 | 45574.4139 | 2024-10-09 | 45574.5903 | 0.0085208 | 3.3546e-05 | 21 | 5334 | Planned | Planned
2123 |  | 36321 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-10-09 | 45574.3958 | 2024-10-09 | 45574.6097 | 0.011808 | 3.8339e-05 | 24 | 7392 | Planned | Planned
2124 |  | 36322 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-10-09 | 45574.4167 | 2024-10-09 | 45574.5118 | 0.013788 | 0.00010064 | 63 | 8631 | Planned | Planned
2125 |  | 36323 | HOWI K10 - K10 FINNERTY AVE | Auckland | HOWI K10 | 2024-10-09 | 45574.3958 | 2024-10-09 | 45574.6111 | 0.026246 | 8.4665e-05 | 53 | 16430 | Planned | Planned
2126 |  | 36324 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2024-10-09 | 45574.375 | 2024-10-09 | 45574.6889 | 0.018773 | 4.1534e-05 | 26 | 11752 | Planned | Planned
2127 |  | 36326 | JAME K10 - K10 HOGANS ROAD | Northern | JAME K10 | 2024-10-09 | 45574.8354 | 2024-10-09 | 45574.8826 | 0.00097765 | 1.4377e-05 | 9 | 612 | Planned | Planned
2128 |  | 36327 | SABU K02 - K02 HEPBURN RD | Northern | SABU K02 | 2024-10-09 | 45574.8958 | 2024-10-09 | 45574.9951 | 0.00022844 | 1.597e-06 | 1 | 143 | Planned | Planned
2129 |  | 36328 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-10 | 45575.3125 | 2024-10-10 | 45575.7153 | 0.029101 | 0.002465 | 781 | 18217 | Planned | Planned
2130 |  | 36329 | BAIR K04 - K04 ASHTON AVENUE | Auckland | BAIR K04 | 2024-10-10 | 45575.3958 | 2024-10-10 | 45575.7507 | 0.35848 | 0.00073004 | 457 | 224407 | Planned | Planned
2131 |  | 36330 | HILL K09 - K09 3 MELROSE RD | Auckland | HILL K09 | 2024-10-10 | 45575.4007 | 2024-10-10 | 45575.6562 | 0.16343 | 0.00044409 | 278 | 102304 | Planned | Planned
2132 |  | 36331 | TRIA K05 - K05 NORTH | Northern | TRIA K05 | 2024-10-10 | 45575.6118 | 2024-10-10 | 45575.6896 | 0.068279 | 0.00079395 | 497 | 42742 | Unplanned | Defective equipment
2133 |  | 36331 | TRIA K05 - K05 NORTH | Northern | TRIA K10 | 2024-10-10 | 45575.6118 | 2024-10-10 | 45575.6896 | 0.14157 | 0.0014042 | 879 | 88620 | Unplanned | Defective equipment
2134 |  | 36331 | TRIA K05 - K05 NORTH | Northern | TRIA K11 | 2024-10-10 | 45575.6118 | 2024-10-10 | 45575.6896 | 0.020631 | 0.00098244 | 615 | 12915 | Unplanned | Defective equipment
2135 |  | 36331 | TRIA K05 - K05 NORTH | Northern | TRIA K12 | 2024-10-10 | 45575.6118 | 2024-10-10 | 45575.6896 | 0.027542 | 0.0013115 | 821 | 17241 | Unplanned | Defective equipment
2136 |  | 36332 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-10-10 | 45575.8042 | 2024-10-10 | 45575.9958 | 0.13497 | 0.00090736 | 568 | 84488 | Unplanned | Defective equipment
2137 |  | 36335 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-10-10 | 45575.9375 | 2024-10-11 | 45576.0924 | 0.004631 | 2.0767e-05 | 13 | 2899 | Planned | Planned
2138 |  | 36336 | NEWT K10 - K10 MT EDEN RD | Auckland | NEWT K10 | 2024-10-10 | 45575.9583 | 2024-10-11 | 45576.1771 | 0.02667 | 8.4665e-05 | 53 | 16695 | Planned | Planned
2139 |  | 36338 | GINN K02 - K02 PADDINGTON ST | Auckland | GINN K02 | 2024-10-11 | 45576.0979 | 2024-10-11 | 45576.1562 | 0.034218 | 0.00040735 | 255 | 21420 | Unplanned | Defective equipment
2140 |  | 36339 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K05 | 2024-10-11 | 45576.2403 | 2024-10-11 | 45576.4014 | 0.045585 | 0.00019649 | 123 | 28536 | Unplanned | Defective equipment
2141 |  | 36339 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K13 | 2024-10-11 | 45576.2403 | 2024-10-11 | 45576.4014 | 0.061764 | 0.00085784 | 537 | 38664 | Unplanned | Defective equipment
2142 |  | 36340 | RBEA K02 - K02 FANTAIL COURT + LS | Northern | RBEA K02 | 2024-10-10 | 45575.9271 | 2024-10-10 | 45575.9306 | 1.5975e-05 | 3.195e-06 | 2 | 10 | Unplanned | Other Cause | Outage caused by Tap Operation
2143 |  | 36341 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-11 | 45576.3125 | 2024-10-11 | 45576.741 | 0.09083 | 0.00066778 | 257 | 56859 | Planned | Planned
2144 |  | 36342 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2024-10-11 | 45576.3542 | 2024-10-11 | 45576.6687 | 0.033288 | 7.3483e-05 | 46 | 20838 | Planned | Planned
2145 |  | 36343 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-10-11 | 45576.5417 | 2024-10-11 | 45576.675 | 0.022299 | 0.00040895 | 256 | 13959 | Planned | Planned
2146 |  | 36344 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K01 | 2024-10-11 | 45576.6917 | 2024-10-11 | 45576.9826 | 0.0089649 | 0.00014697 | 92 | 5612 | Unplanned | Wildlife
2147 |  | 36344 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2024-10-11 | 45576.6917 | 2024-10-11 | 45576.9826 | 0.075363 | 0.0018546 | 1161 | 47177 | Unplanned | Wildlife
2148 |  | 36345 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-10-11 | 45576.7458 | 2024-10-11 | 45576.875 | 0.025561 | 0.00015016 | 94 | 16001 | Unplanned | Defective equipment
2149 |  | 36347 | OTAR K17 - K17 GERALDINE AVE | Auckland | OTAR K17 | 2024-10-12 | 45577.3194 | 2024-10-12 | 45577.7611 | 0.0020256 | 3.195e-06 | 2 | 1268 | Planned | Planned
2150 |  | 36348 | NLYN K11 - K11 GARDENER ROAD | Northern | NLYN K11 | 2024-10-12 | 45577.4271 | 2024-10-12 | 45577.4736 | 0.048913 | 0.00073004 | 457 | 30619 | Unplanned | Defective equipment
2151 |  | 36351 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-10-12 | 45577.4486 | 2024-10-12 | 45577.5521 | 0.00047604 | 3.194e-06 | 2 | 298 | Unplanned | Wildlife
2152 |  | 36352 | MLEO K04 - K04 SPENCES + LS | Northern | MLEO K04 | 2024-10-12 | 45577.5687 | 2024-10-12 | 45577.5729 | 7.6678e-05 | 1.278e-05 | 8 | 48 | Unplanned | Other Cause | Outage caused by Tap Operation
2153 |  | 36353 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-10-12 | 45577.6271 | 2024-10-12 | 45577.691 | 0.0017636 | 1.9169e-05 | 12 | 1104 | Unplanned | Cause unknown
2154 |  | 36354 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-10-12 | 45577.734 | 2024-10-12 | 45577.834 | 0.0020703 | 1.4375e-05 | 9 | 1296 | Unplanned | Defective equipment
2155 |  | 36355 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-12 | 45577.959 | 2024-10-12 | 45577.9632 | 9.585e-06 | 1.597e-06 | 1 | 6 | Unplanned | Other Cause | Outage caused by Tap Operation
2156 |  | 36357 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2024-10-13 | 45578.2507 | 2024-10-13 | 45578.6326 | 0.1029 | 0.00021406 | 134 | 64416 | Unplanned | Third party interference
2157 |  | 36359 | HVAL K02 - K02 CORBAN AVENUE | Northern | HVAL K02 | 2024-10-13 | 45578.3819 | 2024-10-13 | 45578.6819 | 0.020575 | 0.0002556 | 80 | 12880 | Planned | Planned
2158 |  | 36360 | TRIA K03 - K03 COLWILL RD | Northern | TRIA K03 | 2024-10-13 | 45578.409 | 2024-10-13 | 45578.7403 | 0.11095 | 0.0016677 | 1044 | 69457 | Unplanned | Defective equipment
2159 |  | 36361 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-10-13 | 45578.8035 | 2024-10-14 | 45579.1062 | 0.088086 | 0.00024601 | 154 | 55141 | Unplanned | Defective equipment
2160 |  | 36362 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-10-13 | 45578.9583 | 2024-10-14 | 45579.0375 | 0.044799 | 0.00039297 | 246 | 28044 | Planned | Planned
2161 |  | 36363 | OTAR K17 - K17 GERALDINE AVE | Auckland | OTAR K17 | 2024-10-14 | 45579.0833 | 2024-10-14 | 45579.1743 | 0.039553 | 0.00037541 | 210 | 24760 | Planned | Planned
2162 |  | 36364 | MEAS K17 - K17 GRAEME AVE | Auckland | MEAS K17 | 2024-10-14 | 45579.2083 | 2024-10-14 | 45579.2153 | 3.1949e-05 | 3.195e-06 | 2 | 20 | Planned | Planned
2163 |  | 36365 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-10-14 | 45579.2681 | 2024-10-14 | 45579.334 | 0.0015176 | 1.5973e-05 | 10 | 950 | Unplanned | Cause unknown
2164 |  | 36366 | FORR K11 - K11 BLAKEBOROUGH DR + LS | Northern | FORR K02 | 2024-10-14 | 45579.375 | 2024-10-14 | 45579.7375 | 0.014919 | 5.2717e-05 | 33 | 9339 | Planned | Planned
2165 |  | 36366 | FORR K11 - K11 BLAKEBOROUGH DR + LS | Northern | FORR K11 | 2024-10-14 | 45579.375 | 2024-10-14 | 45579.7375 | 0.069988 | 0.00014377 | 90 | 43812 | Planned | Planned
2166 |  | 36367 | MWEL K03 - K03 BRISCOES | Auckland | MWEL K03 | 2024-10-14 | 45579.9583 | 2024-10-15 | 45580.0576 | 0.015077 | 0.00010543 | 66 | 9438 | Planned | Planned
2167 |  | 36368 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-14 | 45579.9931 | 2024-10-15 | 45580.1181 | 0.04573 | 0.0005 | 313 | 28627 | Unplanned | Cause unknown
2168 |  | 36370 | GINN K04 - K04 FARRINGDON ST | Auckland | GINN K04 | 2024-10-15 | 45580.0833 | 2024-10-15 | 45580.0875 | 0.0014856 | 0.00024761 | 155 | 930 | Planned | Planned
2169 |  | 36371 | WEST K12 - K12 PEACH PRODUCTS | Auckland | WEST K12 | 2024-10-15 | 45580.084 | 2024-10-15 | 45580.1653 | 0.056818 | 0.00048563 | 304 | 35568 | Planned | Planned
2170 |  | 36372 | FORR K11 - K11 BLAKEBOROUGH DR + LS | Northern | FORR K11 | 2024-10-15 | 45580.1667 | 2024-10-15 | 45580.2056 | 0.033904 | 0.00060544 | 379 | 21224 | Planned | Planned
2171 |  | 36374 | RBEA K11 - K11 TITAN PL | Northern | RBEA K11 | 2024-10-15 | 45580.3576 | 2024-10-15 | 45580.8562 | 0.14709 | 0.000877 | 549 | 92075 | Unplanned | Defective equipment
2172 |  | 36374 | RBEA K11 - K11 TITAN PL | Northern | SPUR K09 | 2024-10-15 | 45580.3576 | 2024-10-15 | 45580.8562 | 0.0011278 | 0.0005639 | 353 | 706 | Unplanned | Defective equipment
2173 |  | 36375 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-10-15 | 45580.3931 | 2024-10-15 | 45580.7063 | 0.0078803 | 1.7569e-05 | 11 | 4933 | Planned | Planned
2174 |  | 36376 | NEWM K04 - K04 MAHURU ST | Auckland | NEWM K04 | 2024-10-15 | 45580.4056 | 2024-10-15 | 45580.7188 | 0.012968 | 2.8754e-05 | 18 | 8118 | Planned | Planned
2175 |  | 36377 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-10-15 | 45580.3958 | 2024-10-15 | 45580.5444 | 0.0010256 | 4.792e-06 | 3 | 642 | Planned | Planned
2176 |  | 36378 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-10-15 | 45580.4236 | 2024-10-15 | 45580.4882 | 0.003417 | 3.674e-05 | 23 | 2139 | Planned | Planned
2177 |  | 36379 | ATKI K02 - K02 KONINI ROAD | Northern | ATKI K02 | 2024-10-15 | 45580.4965 | 2024-10-15 | 45580.734 | 0.049558 | 0.00020288 | 127 | 31023 | Unplanned | Defective equipment
2178 |  | 36380 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2024-10-15 | 45580.6306 | 2024-10-15 | 45580.7118 | 0.02284 | 0.00021406 | 134 | 14298 | Planned | Planned
2179 |  | 36381 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-15 | 45580.6431 | 2024-10-15 | 45580.6521 | 2.0767e-05 | 1.597e-06 | 1 | 13 | Unplanned | Other Cause | Outage caused by Tap Operation
2180 |  | 36382 | MEAS K17 - K17 GRAEME AVE | Auckland | MEAS K17 | 2024-10-15 | 45580.3854 | 2024-10-16 | 45581.2806 | 0.057985 | 0.0001246 | 78 | 36298 | Planned | Planned
2181 |  | 36383 | MANU K11 - K11 MANUREWA CENTRAL | Auckland | MANU K11 | 2024-10-15 | 45580.9583 | 2024-10-16 | 45581.041 | 0.011786 | 9.9043e-05 | 62 | 7378 | Planned | Planned
2182 |  | 36384 | HOWI K12 - K12 MACLEANS RD | Auckland | HOWI K12 | 2024-10-15 | 45580.9792 | 2024-10-16 | 45581.2201 | 0.05724 | 0.00016614 | 104 | 35832 | Planned | Planned
2183 |  | 36385 | SJOH K05 - K05 69 MERTON RD | Auckland | SJOH K05 | 2024-10-16 | 45581.109 | 2024-10-16 | 45581.1972 | 0.021725 | 0.00063898 | 245 | 13600 | Planned | Planned
2184 |  | 36386 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-10-15 | 45580.8194 | 2024-10-16 | 45581.1465 | 0.085221 | 0.00069008 | 232 | 53348 | Unplanned | Defective equipment
2185 |  | 36387 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-10-15 | 45580.8194 | 2024-10-16 | 45581.5778 | 0.010467 | 9.585e-06 | 6 | 6552 | Unplanned | Defective equipment
2186 |  | 36389 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-16 | 45581.0604 | 2024-10-16 | 45581.1285 | 0.0048307 | 0.0001278 | 80 | 3024 | Unplanned | Defective equipment
2187 |  | 36390 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-10-16 | 45581.3403 | 2024-10-16 | 45581.7014 | 0.041534 | 7.9873e-05 | 50 | 26000 | Planned | Planned
2188 |  | 36391 | HILL K01 - K01 2 HAUGHEY AVE | Auckland | HILL K01 | 2024-10-16 | 45581.3958 | 2024-10-16 | 45581.7438 | 0.07443 | 0.00014856 | 93 | 46593 | Planned | Planned
2189 |  | 36392 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2024-10-16 | 45581.4319 | 2024-10-16 | 45581.5257 | 0.21076 | 0.0024154 | 1512 | 131933 | Unplanned | Defective equipment
2190 |  | 36392 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K19 | 2024-10-16 | 45581.4319 | 2024-10-16 | 45581.5257 | 0.004262 | 4.633e-05 | 29 | 2668 | Unplanned | Defective equipment
2191 |  | 36393 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-10-16 | 45581.375 | 2024-10-16 | 45581.6847 | 0.10117 | 0.00022684 | 142 | 63332 | Planned | Planned
2192 |  | 36394 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2024-10-16 | 45581.6007 | 2024-10-16 | 45581.6312 | 0.023125 | 0.00052556 | 329 | 14476 | Unplanned | Wildlife
2193 |  | 36395 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2024-10-16 | 45581.5299 | 2024-10-24 | 45589.4062 | 0.026342 | 8.4664e-05 | 53 | 16490 | Unplanned | Cause unknown
2194 |  | 36396 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-10-16 | 45581.9167 | 2024-10-17 | 45582.0708 | 0.018441 | 8.3068e-05 | 52 | 11544 | Planned | Planned
2195 |  | 36397 | PAKU K09 - K09 UDYS RD | Auckland | PAKU K09 | 2024-10-16 | 45581.9187 | 2024-10-17 | 45582.1771 | 0.057643 | 0.00015495 | 97 | 36084 | Planned | Planned
2196 |  | 36398 | GINN K01 - K01 WEST TAMAKI RD VIA LS | Auckland | GINN K01 | 2024-10-16 | 45581.9583 | 2024-10-17 | 45582.0618 | 0.028563 | 0.0001917 | 120 | 17880 | Planned | Planned
2197 |  | 36399 | SJOH K09 - K09 168 NORMAN LESSER DR | Auckland | SJOH K09 | 2024-10-17 | 45582.0889 | 2024-10-17 | 45582.1708 | 0.0099905 | 8.4665e-05 | 53 | 6254 | Planned | Planned
2198 |  | 36400 | FORR K11 - K11 BLAKEBOROUGH DR + LS | Northern | FORR K11 | 2024-10-17 | 45582.1667 | 2024-10-17 | 45582.2188 | 0.045288 | 0.00060384 | 378 | 28350 | Planned | Planned
2199 |  | 36401 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-10-17 | 45582.3333 | 2024-10-17 | 45582.7715 | 0.061347 | 0.0029329 | 947 | 38403 | Planned | Planned
2200 |  | 36402 | HVAL K03 - K03 BRUCE McLAREN | Northern | HVAL K03 | 2024-10-17 | 45582.3549 | 2024-10-17 | 45582.6403 | 0.3271 | 0.00083707 | 524 | 204760 | Planned | Planned
2201 |  | 36403 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-10-17 | 45582.375 | 2024-10-17 | 45582.6458 | 0.062301 | 0.00015974 | 100 | 39000 | Planned | Planned
2202 |  | 36404 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-10-17 | 45582.4174 | 2024-10-17 | 45582.6486 | 0.085113 | 0.00025559 | 160 | 53280 | Planned | Planned
2203 |  | 36405 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-10-17 | 45582.4375 | 2024-10-17 | 45582.4653 | 6.3898e-05 | 1.597e-06 | 1 | 40 | Unplanned | Other Cause | Outage caused by Tap Operation
2204 |  | 36406 | FREE K20 - K20 FRANKLIN RD 44 | Auckland | FREE K65 | 2024-10-17 | 45582.875 | 2024-10-18 | 45583.1354 | 0.044329 | 0.00011821 | 74 | 27750 | Planned | Planned
2205 |  | 36407 | TAKP K11 - K11 NORTHCROFT STREET | Northern | TAKP K11 | 2024-10-17 | 45582.9375 | 2024-10-18 | 45583.0924 | 0.03598 | 0.00016134 | 101 | 22523 | Planned | Planned
2206 |  | 36408 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-10-17 | 45582.9792 | 2024-10-18 | 45583.1556 | 0.050844 | 0.00068212 | 269 | 31828 | Planned | Planned
2207 |  | 36409 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-10-18 | 45583.4007 | 2024-10-18 | 45583.5035 | 0.00023642 | 1.597e-06 | 1 | 148 | Planned | Planned
2208 |  | 36410 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-10-18 | 45583.3542 | 2024-10-18 | 45583.7292 | 0.11645 | 0.00021565 | 135 | 72900 | Planned | Planned
2209 |  | 36411 | NLYN K07 - K07 BINSTEAD RD | Northern | NLYN K07 | 2024-10-18 | 45583.3715 | 2024-10-18 | 45583.7361 | 0.039417 | 7.5081e-05 | 47 | 24675 | Planned | Planned
2210 |  | 36412 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-10-18 | 45583.375 | 2024-10-18 | 45583.7347 | 0.091023 | 0.00017572 | 110 | 56980 | Planned | Planned
2211 |  | 36413 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-10-18 | 45583.4194 | 2024-10-18 | 45583.5694 | 0.0041406 | 1.917e-05 | 12 | 2592 | Planned | Planned
2212 |  | 36414 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-10-18 | 45583.4701 | 2024-10-18 | 45583.5104 | 0.0058371 | 0.00010064 | 63 | 3654 | Unplanned | Vegetation
2213 |  | 36415 | RBEA K11 - K11 TITAN PL | Northern | RBEA K11 | 2024-10-18 | 45583.7083 | 2024-10-18 | 45583.9944 | 0.012505 | 3.0352e-05 | 19 | 7828 | Planned | Planned
2214 |  | 36416 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-10-18 | 45583.7764 | 2024-10-18 | 45583.7812 | 0.00036901 | 5.2716e-05 | 33 | 231 | Unplanned | Other Cause | Outage caused by Tap Operation
2215 |  | 36417 | SJOH K06 - K06 60 COLLEGE RD | Auckland | SJOH K06 | 2024-10-18 | 45583.784 | 2024-10-18 | 45583.8889 | 0.0036182 | 2.3962e-05 | 15 | 2265 | Unplanned | Cause unknown
2216 |  | 36418 | MKAU K12 - K12 LAMBIE DRIVE | Auckland | MKAU K12 | 2024-10-19 | 45584.0944 | 2024-10-19 | 45584.2257 | 0.00060384 | 3.195e-06 | 2 | 378 | Planned | Planned
2217 |  | 36419 | WIRI K05 - K05 MERCK, SHARPE & DOHME VIA LS | Auckland | WIRI K05 | 2024-10-19 | 45584.3333 | 2024-10-19 | 45584.5861 | 0.00058148 | 1.597e-06 | 1 | 364 | Planned | Planned
2218 |  | 36420 | HCRE K05 - K05 SHAKESPEARE ROAD + LS | Northern | HCRE K05 | 2024-10-19 | 45584.334 | 2024-10-19 | 45584.6944 | 0.043112 | 8.3068e-05 | 52 | 26988 | Planned | Planned
2219 |  | 36421 | ROSE K15 - K15 BEATRIX ROAD VIA LOCAL | Auckland | ROSE K15 | 2024-10-19 | 45584.3868 | 2024-10-19 | 45584.4264 | 0.10266 | 0.0030959 | 1938 | 64266 | Unplanned | Third party interference
2220 |  | 36422 | MEAS K15 - K15 RAGLAN ST VIA LOCAL SUB | Auckland | MEAS K15 | 2024-10-19 | 45584.3958 | 2024-10-19 | 45584.4979 | 0.0035224 | 2.3962e-05 | 15 | 2205 | Planned | Planned
2221 |  | 36424 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-10-20 | 45585.2597 | 2024-10-20 | 45585.3604 | 0.00023163 | 1.597e-06 | 1 | 145 | Unplanned | Cause unknown
2222 |  | 36425 | NEWM K15 - K15 EDEN ST CARPENTERS | Auckland | NEWM K15 | 2024-10-20 | 45585.9583 | 2024-10-21 | 45586.0486 | 0.026166 | 0.00020128 | 126 | 16380 | Planned | Planned
2223 |  | 36426 | NEWM K01 - K01 EDUCATIONAL DEPT VIA LS | Auckland | NEWM K01 | 2024-10-21 | 45586.0833 | 2024-10-21 | 45586.1799 | 0.058398 | 0.00042013 | 263 | 36557 | Planned | Planned
2224 |  | 36427 | NSBT93C - WAIMAUKU P1028/P1027 - RIVERHEAD H03 (93C) | Northern | WAIM K09 | 2024-10-20 | 45585.8486 | 2024-10-21 | 45586.2514 | 0.034582 | 6.5496e-05 | 41 | 21648 | Planned | Planned
2225 |  | 36430 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-10-21 | 45586.3896 | 2024-10-21 | 45586.5431 | 0.017794 | 0.00023642 | 148 | 11139 | Planned | Planned
2226 |  | 36431 | WAIR K11 - K11 PORANA ROAD | Northern | WAIR K11 | 2024-10-21 | 45586.2771 | 2024-10-22 | 45587.8368 | 0.012524 | 4.473e-05 | 14 | 7840 | Unplanned | Defective equipment
2227 |  | 36432 | ONEH K08 - K08 - TAWA RD | Auckland | ONEH K08 | 2024-10-21 | 45586.4201 | 2024-10-21 | 45586.6396 | 0.24964 | 0.001909 | 1195 | 156271 | Unplanned | Defective equipment
2228 |  | 36433 | RBEA K02 - K02 FANTAIL COURT + LS | Northern | RBEA K02 | 2024-10-21 | 45586.5764 | 2024-10-21 | 45586.6104 | 0.0069665 | 0.00014217 | 89 | 4361 | Unplanned | Wildlife
2229 |  | 36434 | ROCK K17 - K17 ORANGA AVE | Auckland | ROCK K17 | 2024-10-21 | 45586.5125 | 2024-10-21 | 45586.6458 | 0.017176 | 8.9458e-05 | 56 | 10752 | Unplanned | Defective equipment
2230 |  | 36435 | WSWA K06 - K06 ROSKILL RIPPLE | Auckland | WSWA K06 | 2024-10-21 | 45586.6042 | 2024-10-21 | 45586.6806 | 0.055352 | 0.0005032 | 315 | 34650 | Planned | Planned
2231 |  | 36436 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-21 | 45586.6306 | 2024-10-21 | 45586.6813 | 0.0365 | 0.0005 | 313 | 22849 | Unplanned | Cause unknown
2232 |  | 36437 | WEST K18 - K18 MT RICHMOND No.2 | Auckland | WEST K18 | 2024-10-21 | 45586.9375 | 2024-10-22 | 45587.2 | 0.05193 | 0.00013738 | 86 | 32508 | Planned | Planned
2233 |  | 36438 | REMU K08 - K08 McFARLAND ST | Auckland | REMU K08 | 2024-10-21 | 45586.9583 | 2024-10-22 | 45587.0347 | 0.00017572 | 1.597e-06 | 1 | 110 | Planned | Planned
2234 |  | 36439 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-10-21 | 45586.9583 | 2024-10-22 | 45587.0465 | 0.017447 | 0.00013738 | 86 | 10922 | Planned | Planned
2235 |  | 36440 | MCEN K13 - K13 MASCOT AVENUE | Auckland | MCEN K13 | 2024-10-22 | 45587.0833 | 2024-10-22 | 45587.1764 | 0.013382 | 0.0008834 | 278 | 8377 | Planned | Planned
2236 |  | 36442 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-10-21 | 45586.8333 | 2024-10-21 | 45586.8375 | 0.00021086 | 3.5144e-05 | 22 | 132 | Unplanned | Other Cause | Outage caused by Tap Operation
2237 |  | 36443 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-10-22 | 45587.3542 | 2024-10-22 | 45587.7194 | 0.40417 | 0.00076838 | 481 | 253006 | Planned | Planned
2238 |  | 36444 | WAIR K14 - K14 CURRYS LANE | Northern | WAIR K14 | 2024-10-22 | 45587.3958 | 2024-10-22 | 45587.5514 | 0.00035783 | 1.597e-06 | 1 | 224 | Planned | Planned
2239 |  | 36445 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2024-10-22 | 45587.6674 | 2024-10-22 | 45587.7583 | 0.00020927 | 1.597e-06 | 1 | 131 | Unplanned | Cause unknown
2240 |  | 36446 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-10-22 | 45587.8104 | 2024-10-22 | 45587.8514 | 0.0048068 | 8.147e-05 | 51 | 3009 | Unplanned | Vegetation
2241 |  | 36447 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-10-22 | 45587.7132 | 2024-10-22 | 45587.8187 | 0.00024281 | 1.597e-06 | 1 | 152 | Unplanned | Cause unknown
2242 |  | 36448 | HPOI K12 - K12 HOBSONVILLE RD | Northern | HPOI K12 | 2024-10-22 | 45587.9208 | 2024-10-23 | 45588.284 | 0.088549 | 0.0001901 | 119 | 55431 | Planned | Planned
2243 |  | 36449 | WSWA K15 - K15 GRIFFEN RD | Auckland | WSWA K15 | 2024-10-22 | 45587.9583 | 2024-10-23 | 45588.0458 | 0.023147 | 0.00018371 | 115 | 14490 | Planned | Planned
2244 |  | 36450 | WSWA K08 - K08 COMMODORE DRIVE | Auckland | WSWA K08 | 2024-10-23 | 45588.0833 | 2024-10-23 | 45588.1729 | 0.0051518 | 3.9936e-05 | 25 | 3225 | Planned | Planned
2245 |  | 36451 | WAIR K08 - K08 BOND CRESCENT | Northern | WAIR K08 | 2024-10-23 | 45588.3333 | 2024-10-23 | 45588.4542 | 0.047809 | 0.00027476 | 172 | 29928 | Planned | Planned
2246 |  | 36452 | TRIA K03 - K03 COLWILL RD | Northern | TRIA K03 | 2024-10-23 | 45588.4618 | 2024-10-23 | 45588.6118 | 0.03554 | 0.00016454 | 103 | 22248 | Planned | Planned
2247 |  | 36453 | HPOI K07 - K07 POTTERY CRES | Northern | HPOI K07 | 2024-10-23 | 45588.5576 | 2024-10-23 | 45588.6215 | 0.023368 | 0.000254 | 159 | 14628 | Planned | Planned
2248 |  | 36454 | REMU K09 - K09 RANGITOTO AVE | Auckland | REMU K09 | 2024-10-23 | 45588.9583 | 2024-10-24 | 45589.0382 | 0.023515 | 0.00020447 | 128 | 14720 | Planned | Planned
2249 |  | 36455 | CHEV K07 - K07 WALMER RD | Auckland | CHEV K07 | 2024-10-24 | 45589.0833 | 2024-10-24 | 45589.2069 | 0.21781 | 0.0012237 | 766 | 136348 | Planned | Planned
2250 |  | 36457 | HOBV K08 - K08 LUCKENS RD | Northern | HOBV K08 | 2024-10-24 | 45589.3403 | 2024-10-24 | 45589.7431 | 0.06393 | 0.00011022 | 69 | 40020 | Planned | Planned
2251 |  | 36458 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-10-24 | 45589.3438 | 2024-10-24 | 45589.7257 | 0.095768 | 0.00017412 | 109 | 59950 | Planned | Planned
2252 |  | 36459 | REMU K14 - K14 TAHORA AVE | Auckland | REMU K14 | 2024-10-24 | 45589.425 | 2024-10-24 | 45589.5687 | 0.071756 | 0.00034665 | 217 | 44919 | Planned | Planned
2253 |  | 36461 | BROW K12 - K12 OKURA | Northern | BROW K12 | 2024-10-24 | 45589.4326 | 2024-10-24 | 45589.4694 | 0.041232 | 0.00077796 | 487 | 25811 | Unplanned | Cause unknown
2254 |  | 36463 | SNEL K08 - K08 ALGIES BAY | Northern | SNEL K08 | 2024-10-24 | 45589.3333 | 2024-10-24 | 45589.7104 | 0.29611 | 0.00057349 | 359 | 185361 | Planned | Planned
2255 |  | 36464 | HPOI K06 - K06 WISELEY RD | Northern | HPOI K04 | 2024-10-24 | 45589.4326 | 2024-10-24 | 45589.5292 | 0.063283 | 0.00045528 | 285 | 39615 | Planned | Planned
2256 |  | 36465 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K04 | 2024-10-24 | 45589.3306 | 2024-10-24 | 45589.3424 | 0.0045432 | 0.00037858 | 237 | 2844 | Unplanned | Human error
2257 |  | 36465 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-10-24 | 45589.3306 | 2024-10-24 | 45589.3424 | 0.024924 | 0.0014903 | 933 | 15602 | Unplanned | Human error
2258 |  | 36466 | SJOH K06 - K06 60 COLLEGE RD | Auckland | SJOH K06 | 2024-10-24 | 45589.9792 | 2024-10-25 | 45590.1951 | 0.092407 | 0.00029713 | 186 | 57846 | Planned | Planned
2259 |  | 36467 | HOWI K12 - K12 MACLEANS RD | Auckland | HOWI K12 | 2024-10-24 | 45589.9826 | 2024-10-25 | 45590.1882 | 0.048745 | 0.00016774 | 105 | 30514 | Planned | Planned
2260 |  | 36469 | JAME K01 - K01 WELDENE | Northern | JAME K01 | 2024-10-24 | 45589.8958 | 2024-10-25 | 45590.0007 | 0.00024122 | 1.597e-06 | 1 | 151 | Planned | Planned
2261 |  | 36470 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-10-24 | 45589.9167 | 2024-10-25 | 45590.0222 | 0.12704 | 0.0013003 | 814 | 79529 | Unplanned | Defective equipment
2262 |  | 36471 | SHEL - St Heliers | Auckland | SHEL K04 | 2024-10-24 | 45589.9646 | 2024-10-25 | 45590.1701 | 0.033035 | 0.0033035 | 2068 | 20680 | Unplanned | Defective equipment
2263 |  | 36471 | SHEL - St Heliers | Auckland | SHEL K05 | 2024-10-24 | 45589.9646 | 2024-10-25 | 45590.1701 | 0.025591 | 0.0021326 | 1335 | 16020 | Unplanned | Defective equipment
2264 |  | 36471 | SHEL - St Heliers | Auckland | SHEL K06 | 2024-10-24 | 45589.9646 | 2024-10-25 | 45590.1701 | 0.55667 | 0.0030719 | 1923 | 348474 | Unplanned | Defective equipment
2265 |  | 36471 | SHEL - St Heliers | Auckland | SHEL K09 | 2024-10-24 | 45589.9646 | 2024-10-25 | 45590.1701 | 0.0012668 | 0.0012668 | 793 | 793 | Unplanned | Defective equipment
2266 |  | 36472 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-10-25 | 45590.1444 | 2024-10-25 | 45590.1889 | 0.021751 | 0.00095689 | 599 | 13616 | Unplanned | Cause unknown
2267 |  | 36473 | KING K02 - K02 KINGSLAND AVE | Auckland | KING K02 | 2024-10-25 | 45590.1715 | 2024-10-25 | 45590.4104 | 0.14125 | 0.00087861 | 405 | 88421 | Unplanned | Defective equipment
2268 |  | 36474 | SHEL K09 - K09 BARDSEY ST | Auckland | SHEL K09 | 2024-10-25 | 45590.2167 | 2024-10-25 | 45590.2604 | 0.036331 | 0.00057668 | 361 | 22743 | Unplanned | Defective equipment
2269 |  | 36475 | SAND K11 - K11 BEAGLE AVE | Auckland | SAND K11 | 2024-10-25 | 45590.375 | 2024-10-25 | 45590.6632 | 0.0013259 | 3.195e-06 | 2 | 830 | Planned | Planned
2270 |  | 36476 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-10-25 | 45590.3597 | 2024-10-25 | 45590.7292 | 0.20736 | 0.00038978 | 244 | 129808 | Planned | Planned
2271 |  | 36477 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-10-25 | 45590.3958 | 2024-10-25 | 45590.6194 | 0.0061726 | 1.917e-05 | 12 | 3864 | Planned | Planned
2272 |  | 36479 | TATA K01 - K01 WINSTON PL | Northern | TATA K01 | 2024-10-25 | 45590.875 | 2024-10-26 | 45591.0715 | 0.0076854 | 2.7156e-05 | 17 | 4811 | Planned | Planned
2273 |  | 36480 | MCEN K12 - K12 ROBERTSON ROAD SOUTH | Auckland | MCEN K12 | 2024-10-26 | 45591.0938 | 2024-10-26 | 45591.2486 | 0.18518 | 0.0015304 | 958 | 115922 | Unplanned | Third party interference
2274 |  | 36481 | TRIA K12 - K12 UNIVERSAL DRIVE | Northern | TRIA K12 | 2024-10-26 | 45591.3979 | 2024-10-26 | 45591.6625 | 0.070601 | 0.00018531 | 116 | 44196 | Unplanned | Defective equipment
2275 |  | 36482 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-10-26 | 45591.3542 | 2024-10-26 | 45591.6597 | 0.054825 | 0.0001246 | 78 | 34320 | Planned | Planned
2276 |  | 36486 | MANU K04 - K04 CENTRE WEYMOUTH RD VIA LS | Auckland | MANU K04 | 2024-10-26 | 45591.7083 | 2024-10-26 | 45591.7521 | 0.03613 | 0.00057349 | 359 | 22617 | Unplanned | Defective equipment
2277 |  | 36487 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-10-26 | 45591.7326 | 2024-10-26 | 45591.9229 | 0.061041 | 0.00085944 | 538 | 38211 | Unplanned | Vegetation
2278 |  | 36488 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-10-26 | 45591.7306 | 2024-10-26 | 45591.7688 | 0.023494 | 0.00062783 | 393 | 14707 | Unplanned | Vegetation
2279 |  | 36490 | REMU K08 - K08 McFARLAND ST | Auckland | REMU K08 | 2024-10-26 | 45591.9583 | 2024-10-27 | 45592.0694 | 0.00025559 | 1.597e-06 | 1 | 160 | Planned | Planned
2280 |  | 36492 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-10-26 | 45591.9736 | 2024-10-26 | 45591.9854 | 0.023844 | 0.0014026 | 878 | 14926 | Unplanned | Third party interference
2281 |  | 36493 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-10-27 | 45592.1049 | 2024-10-27 | 45592.1771 | 0.0064793 | 6.23e-05 | 39 | 4056 | Unplanned | Cause unknown
2282 |  | 36494 | HAUR K04 - K04 CLIFTON ROAD + LS | Northern | HAUR K04 | 2024-10-27 | 45592.3556 | 2024-10-27 | 45592.691 | 0.040122 | 8.3068e-05 | 52 | 25116 | Planned | Planned
2283 |  | 36497 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-10-27 | 45592.2771 | 2024-10-27 | 45592.3771 | 0.016562 | 0.00011501 | 72 | 10368 | Unplanned | Cause unknown
2284 |  | 36498 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-10-27 | 45592.3757 | 2024-10-27 | 45592.7479 | 0.035106 | 6.5494e-05 | 41 | 21976 | Planned | Planned
2285 |  | 36499 | TATA K11 - K11 YEOVIL ROAD | Northern | TATA K11 | 2024-10-27 | 45592.5104 | 2024-10-27 | 45592.7542 | 0.24439 | 0.0032444 | 2031 | 152989 | Unplanned | Third party interference
2286 |  | 36502 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-10-28 | 45593.3104 | 2024-10-28 | 45593.3688 | 0.00026837 | 3.195e-06 | 2 | 168 | Unplanned | Cause unknown
2287 |  | 36503 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-28 | 45593.3333 | 2024-10-28 | 45593.3972 | 0.00014697 | 1.597e-06 | 1 | 92 | Unplanned | Cause unknown
2288 |  | 36508 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-10-28 | 45593.8243 | 2024-10-28 | 45593.8896 | 0.00030032 | 3.195e-06 | 2 | 188 | Unplanned | Defective equipment
2289 |  | 36511 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-10-29 | 45594.3694 | 2024-10-29 | 45594.4389 | 0.00031949 | 3.195e-06 | 2 | 200 | Unplanned | Defective equipment
2290 |  | 36512 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-10-29 | 45594.375 | 2024-10-29 | 45594.641 | 0.0030591 | 7.987e-06 | 5 | 1915 | Planned | Planned
2291 |  | 36513 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-29 | 45594.3986 | 2024-10-29 | 45594.5889 | 0.0013131 | 4.792e-06 | 3 | 822 | Planned | Planned
2292 |  | 36514 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-10-29 | 45594.4167 | 2024-10-29 | 45594.4229 | 0.00064697 | 7.1881e-05 | 45 | 405 | Planned | Planned
2293 |  | 36515 | MWEL K14 - K14 JELICOE RD | Auckland | MWEL K14 | 2024-10-29 | 45594.5208 | 2024-11-01 | 45597.6771 | 0.0072605 | 1.597e-06 | 1 | 4545 | Unplanned | Cause unknown
2294 |  | 36516 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-10-29 | 45594.7708 | 2024-10-30 | 45595.5306 | 0.090419 | 0.00062939 | 372 | 56602 | Unplanned | Defective equipment
2295 |  | 36517 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-10-29 | 45594.8535 | 2024-10-29 | 45594.9042 | 0.080327 | 0.003548 | 2221 | 50284 | Unplanned | Cause unknown
2296 |  | 36519 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-10-30 | 45595.0194 | 2024-10-30 | 45595.1493 | 0.010799 | 0.00077478 | 246 | 6760 | Unplanned | Wildlife
2297 |  | 36520 | TPAP K17 - K17 PATRICK ST | Auckland | TPAP K17 | 2024-10-30 | 45595.0417 | 2024-10-30 | 45595.1097 | 0.0084538 | 8.6259e-05 | 54 | 5292 | Unplanned | Defective equipment
2298 |  | 36521 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-10-30 | 45595.0854 | 2024-10-30 | 45595.1826 | 0.026141 | 0.00052235 | 327 | 16364 | Unplanned | Cause unknown
2299 |  | 36524 | RBEA K06 - K06 VIPOND RD | Northern | RBEA K06 | 2024-10-30 | 45595.1722 | 2024-10-30 | 45595.3125 | 0.013876 | 6.8691e-05 | 43 | 8686 | Unplanned | Vegetation
2300 |  | 36525 | BMON K01 - K01 ACHILLES CRESCENT | Northern | BMON K01 | 2024-10-30 | 45595.3764 | 2024-10-30 | 45595.6486 | 0.090316 | 0.00023642 | 148 | 56537 | Planned | Planned
2301 |  | 36526 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-10-30 | 45595.3403 | 2024-10-30 | 45595.6722 | 0.022144 | 4.6325e-05 | 29 | 13862 | Planned | Planned
2302 |  | 36527 | WAIA K02 - K02 FIRTH ROAD | Northern | WAIA K02 | 2024-10-30 | 45595.3354 | 2024-10-30 | 45595.7153 | 0.028836 | 5.2716e-05 | 33 | 18051 | Planned | Planned
2303 |  | 36529 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-10-30 | 45595.3757 | 2024-10-30 | 45595.566 | 0.013131 | 4.7924e-05 | 30 | 8220 | Planned | Planned
2304 |  | 36530 | WAIA K02 - K02 FIRTH ROAD | Northern | WAIA K02 | 2024-10-30 | 45595.6514 | 2024-10-30 | 45595.6847 | 0.0081279 | 0.00016933 | 106 | 5088 | Unplanned | Defective equipment
2305 |  | 36531 | MWEL K03 - K03 BRISCOES | Auckland | MWEL K03 | 2024-10-30 | 45595.7493 | 2024-10-30 | 45595.7562 | 0.0038978 | 0.00038978 | 244 | 2440 | Unplanned | Third party interference
2306 |  | 36532 | PAKU K09 - K09 UDYS RD | Auckland | PAKU K09 | 2024-10-30 | 45595.9167 | 2024-10-31 | 45596.1979 | 0.062109 | 0.00015336 | 96 | 38880 | Planned | Planned
2307 |  | 36533 | WAIR K14 - K14 CURRYS LANE | Northern | WAIR K14 | 2024-10-30 | 45595.9375 | 2024-10-31 | 45596.0701 | 0.019527 | 0.00010224 | 64 | 12224 | Planned | Planned
2308 |  | 36534 | NEWT K22 - K22 HOHIPERE ST | Auckland | NEWT K22 | 2024-10-30 | 45595.9201 | 2024-10-31 | 45596.1937 | 0.019511 | 4.9521e-05 | 31 | 12214 | Planned | Planned
2309 |  | 36535 | PAPA K09 - K09 LAURIE AVE | Auckland | PAPA K09 | 2024-10-31 | 45596.1222 | 2024-10-31 | 45596.1424 | 0.025638 | 0.00099203 | 621 | 16049 | Unplanned | Third party interference
2310 |  | 36536 | NLYN K07 - K07 BINSTEAD RD | Northern | NLYN K07 | 2024-10-31 | 45596.2514 | 2024-10-31 | 45596.5285 | 0.083907 | 0.0016007 | 793 | 52525 | Unplanned | Wildlife
2311 |  | 36537 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-10-31 | 45596.3354 | 2024-10-31 | 45596.6944 | 0.064419 | 0.0001246 | 78 | 40326 | Planned | Planned
2312 |  | 36538 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2024-10-31 | 45596.3375 | 2024-10-31 | 45596.6958 | 0.022032 | 0.00014377 | 90 | 13792 | Planned | Planned
2313 |  | 36539 | WARK K10 - K10 WOODCOCKS | Northern | WARK K10 | 2024-10-31 | 45596.1771 | 2024-10-31 | 45596.5201 | 0.016572 | 3.3547e-05 | 21 | 10374 | Unplanned | Defective equipment
2314 |  | 36540 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-10-31 | 45596.4236 | 2024-10-31 | 45596.5215 | 0.015992 | 0.00011342 | 71 | 10011 | Planned | Planned
2315 |  | 36541 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-10-31 | 45596.4167 | 2024-10-31 | 45596.5264 | 0.0005048 | 3.195e-06 | 2 | 316 | Planned | Planned
2316 |  | 36542 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-10-31 | 45596.9167 | 2024-11-01 | 45597.0312 | 0.0021086 | 1.278e-05 | 8 | 1320 | Planned | Planned
2317 |  | 36543 | WEST K12 - K12 PEACH PRODUCTS | Auckland | WEST K12 | 2024-10-31 | 45596.9583 | 2024-11-01 | 45597.1875 | 0.068004 | 0.00020607 | 129 | 42570 | Planned | Planned
2318 |  | 36544 | AVON K03 - K03 9 ELM ST (C-4229) | Auckland | AVON K03 | 2024-10-31 | 45596.9792 | 2024-11-01 | 45597.2278 | 0.048601 | 0.00090736 | 568 | 30424 | Planned | Planned
2319 |  | 36548 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-11-01 | 45597.3958 | 2024-11-01 | 45597.5896 | 0.0013371 | 4.792e-06 | 3 | 837 | Planned | Planned
2320 |  | 36549 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-11-01 | 45597.3354 | 2024-11-01 | 45597.6736 | 0.063793 | 0.00013099 | 82 | 39934 | Planned | Planned
2321 |  | 36550 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-11-01 | 45597.3958 | 2024-11-01 | 45597.7243 | 0.024935 | 5.2716e-05 | 33 | 15609 | Planned | Planned
2322 |  | 36551 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2024-11-01 | 45597.5903 | 2024-11-01 | 45597.6194 | 0.00033547 | 7.987e-06 | 5 | 210 | Unplanned | Defective equipment
2323 |  | 36552 | BROW K04 - K04 NORTHCROSS | Northern | BROW K04 | 2024-11-01 | 45597.5514 | 2024-11-01 | 45597.6778 | 0.041866 | 0.00023003 | 144 | 26208 | Unplanned | Wildlife
2324 |  | 36553 | RBEA K13 - K13 CDC SILVERDALE #2 | Northern | RBEA K13 | 2024-11-01 | 45597.7097 | 2024-11-01 | 45597.784 | 0.00017093 | 1.597e-06 | 1 | 107 | Unplanned | Third party interference
2325 |  | 36554 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-11-01 | 45597.9187 | 2024-11-01 | 45597.9938 | 0.012249 | 0.00011342 | 71 | 7668 | Planned | Planned
2326 |  | 36555 | ONEH K02 - K02 - GALWAY ST | Auckland | ONEH K02 | 2024-11-01 | 45597.9597 | 2024-11-02 | 45598.2208 | 0.24206 | 0.00064377 | 403 | 151528 | Planned | Planned
2327 |  | 36556 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-11-02 | 45598.1743 | 2024-11-02 | 45598.2736 | 0.036321 | 0.000254 | 159 | 22737 | Planned | Planned
2328 |  | 36557 | HAUR K04 - K04 CLIFTON ROAD + LS | Northern | HAUR K04 | 2024-11-02 | 45598.2417 | 2024-11-02 | 45598.7979 | 0.34155 | 0.0023371 | 1463 | 213810 | Unplanned | Third party interference
2329 |  | 36558 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-02 | 45598.4785 | 2024-11-02 | 45598.6056 | 0.025593 | 0.00025719 | 161 | 16021 | Unplanned | Defective equipment
2330 |  | 36559 | GHIT K07 - K07 BLACKS RD | Northern | GHIT K05 | 2024-11-02 | 45598.6229 | 2024-11-02 | 45598.9604 | 0.043275 | 0.00020128 | 126 | 27090 | Unplanned | Defective equipment
2331 |  | 36559 | GHIT K07 - K07 BLACKS RD | Northern | GHIT K07 | 2024-11-02 | 45598.6229 | 2024-11-02 | 45598.9604 | 0.15708 | 0.00049361 | 309 | 98332 | Unplanned | Defective equipment
2332 |  | 36560 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-11-02 | 45598.8562 | 2024-11-02 | 45598.9201 | 0.00058787 | 6.39e-06 | 4 | 368 | Unplanned | Cause unknown
2333 |  | 36561 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-11-03 | 45599.466 | 2024-11-03 | 45599.7917 | 0.11349 | 0.0019633 | 1229 | 71047 | Unplanned | Vegetation
2334 |  | 36562 | WAIA K05 - K05 CARLISE ROAD | Northern | WAIA K05 | 2024-11-03 | 45599.5736 | 2024-11-03 | 45599.6146 | 0.004524 | 7.6678e-05 | 48 | 2832 | Unplanned | Defective equipment
2335 |  | 36563 | NEWT K12 - K12 AIR NEW ZEALAND COMPUTER CENTRE | Auckland | NEWT K12 | 2024-11-04 | 45600.0868 | 2024-11-04 | 45600.1667 | 0.017085 | 0.00014856 | 93 | 10695 | Planned | Planned
2336 |  | 36564 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-11-03 | 45599.9583 | 2024-11-04 | 45600.0451 | 0.0035943 | 2.8754e-05 | 18 | 2250 | Planned | Planned
2337 |  | 36565 | HCRE K13 - K13 SUNNYBRAE ROAD | Northern | HCRE K13 | 2024-11-03 | 45599.9639 | 2024-11-04 | 45600.0326 | 0.0023722 | 2.3962e-05 | 15 | 1485 | Unplanned | Defective equipment
2338 |  | 36566 | RBEA K11 - K11 TITAN PL | Northern | RBEA K11 | 2024-11-04 | 45600.1285 | 2024-11-04 | 45600.1729 | 0.055924 | 0.00087381 | 547 | 35008 | Unplanned | Cause unknown
2339 |  | 36567 | WSWA K05 - K05 RICHARDSON RD O/H LINE EAST VIA LS | Auckland | WSWA K05 | 2024-11-04 | 45600.4167 | 2024-11-04 | 45600.6549 | 0.063999 | 0.00021086 | 132 | 40063 | Planned | Planned
2340 |  | 36568 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-11-04 | 45600.375 | 2024-11-04 | 45600.6278 | 0.36749 | 0.0010096 | 632 | 230048 | Planned | Planned
2341 |  | 36569 | SUNS K05 - K05 MEADOWOOD DRIVE | Northern | SUNS K05 | 2024-11-04 | 45600.3924 | 2024-11-04 | 45600.6604 | 0.24363 | 0.0021694 | 1358 | 152514 | Unplanned | Defective equipment
2342 |  | 36570 | RBEA K11 - K11 TITAN PL | Northern | RBEA K11 | 2024-11-04 | 45600.4472 | 2024-11-04 | 45600.5292 | 0.0028275 | 2.3961e-05 | 15 | 1770 | Unplanned | Defective equipment
2343 |  | 36571 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-11-04 | 45600.4222 | 2024-11-04 | 45600.791 | 0.01442 | 2.7157e-05 | 17 | 9027 | Unplanned | Third party interference
2344 |  | 36572 | SABU K01 - K01 ST LEONARDS RD + LS | Northern | SABU K01 | 2024-11-04 | 45600.4271 | 2024-11-04 | 45600.5208 | 0.051542 | 0.00038179 | 239 | 32265 | Unplanned | Cause unknown
2345 |  | 36573 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-11-04 | 45600.5375 | 2024-11-04 | 45600.6201 | 0.020775 | 0.00068053 | 426 | 13005 | Unplanned | Human error
2346 |  | 36574 | QUAY K23 - K23 SOFRANA HOUSE | Auckland | QUAY K23 | 2024-11-04 | 45600.9375 | 2024-11-05 | 45601.1215 | 0.024553 | 9.2653e-05 | 58 | 15370 | Planned | Planned
2347 |  | 36575 | LIVE K24 - K24 AIREDALE ST TELEPHONE EX | Auckland | LIVE K24 | 2024-11-04 | 45600.9757 | 2024-11-05 | 45601.0444 | 0.00015815 | 1.597e-06 | 1 | 99 | Planned | Planned
2348 |  | 36577 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K07 | 2024-11-04 | 45600.9799 | 2024-11-05 | 45601.209 | 0.037428 | 0.00011342 | 71 | 23430 | Planned | Planned
2349 |  | 36578 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-11-04 | 45600.8403 | 2024-11-14 | 45610.4271 | 0 | 0 | 0 | 0 | Unplanned | Third party interference
2350 |  | 36579 | GINN K06 - K06 MERFIELD ST | Auckland | GINN K06 | 2024-11-05 | 45601.0833 | 2024-11-05 | 45601.1632 | 0.0022045 | 1.917e-05 | 12 | 1380 | Planned | Planned
2351 |  | 36580 | MKAU K12 - K12 LAMBIE DRIVE | Auckland | MKAU K12 | 2024-11-05 | 45601.2389 | 2024-11-05 | 45601.6972 | 0.20792 | 0.0026901 | 1684 | 130154 | Unplanned | Third party interference
2352 |  | 36581 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-05 | 45601.3569 | 2024-11-05 | 45601.7076 | 0.06131 | 0.0001214 | 76 | 38380 | Planned | Planned
2353 |  | 36582 | HPOI K07 - K07 POTTERY CRES | Northern | HPOI K07 | 2024-11-05 | 45601.3764 | 2024-11-05 | 45601.5278 | 0.00069649 | 3.195e-06 | 2 | 436 | Unplanned | Defective equipment
2354 |  | 36583 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-11-05 | 45601.4722 | 2024-11-05 | 45601.5597 | 0.0020128 | 1.5974e-05 | 10 | 1260 | Unplanned | Defective equipment
2355 |  | 36585 | FREE K13 - K13 WILKINS ST (5) | Auckland | FREE K56 | 2024-11-05 | 45601.9583 | 2024-11-06 | 45602.0479 | 0.0035032 | 2.7157e-05 | 17 | 2193 | Planned | Planned
2356 |  | 36586 | NEWT K25 - K25 KYBER PASS RD EDEN HOUSE VIA LS | Auckland | NEWT K25 | 2024-11-06 | 45602.0889 | 2024-11-06 | 45602.1632 | 0.010085 | 9.425e-05 | 59 | 6313 | Planned | Planned
2357 |  | 36587 | NCOT K01 - K01 EXMOUTH | Northern | NCOT K01 | 2024-11-06 | 45602.3528 | 2024-11-06 | 45602.3951 | 0.039972 | 0.0014409 | 902 | 25022 | Unplanned | Cause unknown
2358 |  | 36588 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-11-06 | 45602.3542 | 2024-11-06 | 45602.7299 | 0.011719 | 2.2364e-05 | 14 | 7336 | Planned | Planned
2359 |  | 36589 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-11-06 | 45602.3819 | 2024-11-06 | 45602.6493 | 0.023371 | 6.0703e-05 | 38 | 14630 | Planned | Planned
2360 |  | 36590 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K07 | 2024-11-06 | 45602.3993 | 2024-11-06 | 45602.5771 | 0.021499 | 0.00014856 | 93 | 13458 | Planned | Planned
2361 |  | 36591 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-11-06 | 45602.3688 | 2024-11-07 | 45603.484 | 0.0025655 | 1.597e-06 | 1 | 1606 | Planned | Planned
2362 |  | 36592 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-06 | 45602.4167 | 2024-11-06 | 45602.616 | 0.036678 | 0.00012779 | 80 | 22960 | Planned | Planned
2363 |  | 36593 | MNAB K02 - K02 GAVIN ST WEST | Auckland | MNAB K02 | 2024-11-06 | 45602.9583 | 2024-11-07 | 45603.0542 | 0.12059 | 0.00087381 | 547 | 75486 | Planned | Planned
2364 |  | 36594 | PAKU K01 - K01 BEECHDALE CRES | Auckland | PAKU K01 | 2024-11-07 | 45603.0417 | 2024-11-07 | 45603.1285 | 0.031949 | 0.00025559 | 160 | 20000 | Planned | Planned
2365 |  | 36595 | GINN K01 - K01 WEST TAMAKI RD VIA LS | Auckland | GINN K01 | 2024-11-07 | 45603.0833 | 2024-11-07 | 45603.1653 | 0.096889 | 0.00082109 | 514 | 60652 | Planned | Planned
2366 |  | 36596 | MANL K05 - K05 ARKLES BAY | Northern | MANL K05 | 2024-11-06 | 45602.9167 | 2024-11-07 | 45603.1264 | 0.012543 | 4.1533e-05 | 26 | 7852 | Planned | Planned
2367 |  | 36597 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-11-07 | 45603.3333 | 2024-11-07 | 45603.709 | 0.021606 | 3.9936e-05 | 25 | 13525 | Planned | Planned
2368 |  | 36598 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-11-07 | 45603.3764 | 2024-11-07 | 45603.6319 | 0.049381 | 0.00013419 | 84 | 30912 | Planned | Planned
2369 |  | 36599 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2024-11-07 | 45603.3333 | 2024-11-07 | 45603.6632 | 0.0015176 | 3.195e-06 | 2 | 950 | Planned | Planned
2370 |  | 36600 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-11-07 | 45603.3785 | 2024-11-07 | 45603.6806 | 0.022237 | 5.1119e-05 | 32 | 13920 | Planned | Planned
2371 |  | 36601 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-11-07 | 45603.4167 | 2024-11-07 | 45603.5347 | 0.011134 | 6.5496e-05 | 41 | 6970 | Planned | Planned
2372 |  | 36602 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-11-07 | 45603.6188 | 2024-11-08 | 45604.7812 | 0.045777 | 0.00016454 | 54 | 28656 | Unplanned | Vegetation
2373 |  | 36603 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-11-07 | 45603.5611 | 2024-11-07 | 45603.6951 | 0.00092493 | 4.792e-06 | 3 | 579 | Unplanned | Vegetation
2374 |  | 36604 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2024-11-07 | 45603.691 | 2024-11-07 | 45603.8299 | 0.024281 | 0.00012141 | 76 | 15200 | Unplanned | Defective equipment
2375 |  | 36606 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2024-11-07 | 45603.9167 | 2024-11-08 | 45604.0451 | 0.0026598 | 1.4377e-05 | 9 | 1665 | Planned | Planned
2376 |  | 36607 | REMU K10 - K10 LADIES MILE | Auckland | REMU K10 | 2024-11-07 | 45603.9792 | 2024-11-08 | 45604.1625 | 0.075953 | 0.0012061 | 462 | 47546 | Planned | Planned
2377 |  | 36610 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-11-08 | 45604.3611 | 2024-11-08 | 45604.6931 | 0.063378 | 0.00013259 | 83 | 39674 | Planned | Planned
2378 |  | 36611 | CARB K13 - K13 PANAMA RD | Auckland | CARB K13 | 2024-11-08 | 45604.3993 | 2024-11-08 | 45604.7229 | 0.040198 | 8.6263e-05 | 54 | 25164 | Planned | Planned
2379 |  | 36612 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-11-08 | 45604.4403 | 2024-11-08 | 45604.4889 | 0.00033547 | 4.792e-06 | 3 | 210 | Planned | Planned
2380 |  | 36613 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-11-08 | 45604.8549 | 2024-11-08 | 45604.925 | 0.0017748 | 1.7572e-05 | 11 | 1111 | Unplanned | Cause unknown
2381 |  | 36614 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-11-08 | 45604.9583 | 2024-11-09 | 45605.2361 | 0.067732 | 0.00016933 | 106 | 42400 | Planned | Planned
2382 |  | 36615 | MANL K02 - K02 STANMORE BAY | Northern | MANL K02 | 2024-11-08 | 45604.9486 | 2024-11-08 | 45604.95 | 7.9873e-05 | 3.9936e-05 | 25 | 50 | Unplanned | Other Cause | Outage caused by Tap Operation
2383 |  | 36616 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-11-08 | 45604.9583 | 2024-11-09 | 45605.1319 | 0.12061 | 0.00048243 | 302 | 75500 | Planned | Planned
2384 |  | 36617 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-11-09 | 45605.3278 | 2024-11-09 | 45605.3785 | 0.00011661 | 1.597e-06 | 1 | 73 | Unplanned | Cause unknown
2385 |  | 36618 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2024-11-10 | 45606.2438 | 2024-11-10 | 45606.3194 | 0.0073132 | 6.7091e-05 | 42 | 4578 | Unplanned | Cause unknown
2386 |  | 36619 | WOOD K05 - K05 FAIRDENE AVE | Northern | WOOD K05 | 2024-11-10 | 45606.3472 | 2024-11-10 | 45606.3854 | 0.042349 | 0.00076997 | 482 | 26510 | Unplanned | Wildlife
2387 |  | 36620 | DRIV K16 - K16 MANUKAU RD | Auckland | DRIV K16 | 2024-11-10 | 45606.3972 | 2024-11-10 | 45606.559 | 0.15592 | 0.0019984 | 1251 | 97605 | Unplanned | Defective equipment
2388 |  | 36621 | MKIN K04 - K04 COLISEUM DRIVE | Northern | MKIN K04 | 2024-11-10 | 45606.534 | 2024-11-10 | 45606.7722 | 0.00054793 | 1.597e-06 | 1 | 343 | Unplanned | Defective equipment
2389 |  | 36622 | DRIV K03 - K03 DOMETT AVE | Auckland | DRIV K03 | 2024-11-10 | 45606.9583 | 2024-11-11 | 45607.0347 | 0.023371 | 0.00021246 | 133 | 14630 | Planned | Planned
2390 |  | 36623 | PAKU K05 - K05 GLENMORE RD | Auckland | PAKU K05 | 2024-11-11 | 45607.084 | 2024-11-11 | 45607.1653 | 0.029157 | 0.0002492 | 156 | 18252 | Planned | Planned
2391 |  | 36625 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-11-11 | 45607.1819 | 2024-11-11 | 45607.2625 | 0.07301 | 0.00062939 | 394 | 45704 | Unplanned | Vegetation
2392 |  | 36626 | PAPA K06 - K06 13 PORCHESTER RD | Auckland | PAPA K06 | 2024-11-11 | 45607.3938 | 2024-11-13 | 45609.6042 | 0.0050847 | 1.597e-06 | 1 | 3183 | Unplanned | Defective equipment
2393 |  | 36627 | OTAR K17 - K17 GERALDINE AVE | Auckland | OTAR K17 | 2024-11-11 | 45607.9396 | 2024-11-23 | 45619.2479 | 0.026476 | 7.9875e-05 | 25 | 16574 | Planned | Planned
2394 |  | 36628 | HPOI K06 - K06 WISELEY RD | Northern | HPOI K06 | 2024-11-12 | 45608.3354 | 2024-11-12 | 45608.5903 | 0.051592 | 0.00014058 | 88 | 32296 | Planned | Planned
2395 |  | 36629 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-11-12 | 45608.375 | 2024-11-12 | 45608.5104 | 0.0065416 | 3.3547e-05 | 21 | 4095 | Planned | Planned
2396 |  | 36630 | BIRK K03 - K03 ESKDALE ROAD | Northern | BIRK K03 | 2024-11-12 | 45608.4368 | 2024-11-12 | 45608.475 | 0.0036023 | 6.5496e-05 | 41 | 2255 | Unplanned | Wildlife
2397 |  | 36631 | HILL K09 - K09 3 MELROSE RD | Auckland | HILL K09 | 2024-11-12 | 45608.4688 | 2024-11-12 | 45608.4757 | 0.00092653 | 9.2653e-05 | 58 | 580 | Unplanned | Other Cause | Outage caused by Tap Operation
2398 |  | 36632 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-11-12 | 45608.9792 | 2024-11-13 | 45609.141 | 0.076303 | 0.00032748 | 205 | 47765 | Planned | Planned
2399 |  | 36633 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K07 | 2024-11-12 | 45608.9799 | 2024-11-13 | 45609.1715 | 0.031304 | 0.00011342 | 71 | 19596 | Planned | Planned
2400 |  | 36635 | HOWI K04 - K04 HIGHLAND PARK MOTORS | Auckland | HOWI K04 | 2024-11-13 | 45609.2431 | 2024-11-13 | 45609.2604 | 0.0026358 | 0.00010543 | 66 | 1650 | Planned | Planned
2401 |  | 36637 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-11-13 | 45609.3368 | 2024-11-13 | 45609.7292 | 0.057764 | 0.00010224 | 64 | 36160 | Planned | Planned
2402 |  | 36638 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-11-13 | 45609.4653 | 2024-11-13 | 45609.6472 | 0.041833 | 0.00017892 | 112 | 26187 | Planned | Planned
2403 |  | 36639 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-11-13 | 45609.4951 | 2024-11-13 | 45609.5868 | 0.016182 | 0.00064858 | 406 | 10130 | Unplanned | Wildlife
2404 |  | 36640 | SUNS K05 - K05 MEADOWOOD DRIVE | Northern | SUNS K05 | 2024-11-13 | 45609.5986 | 2024-11-13 | 45609.6951 | 0.072165 | 0.00051917 | 325 | 45175 | Planned | Planned
2405 |  | 36641 | MWEL K06 - K06 WAIPUNA RD 58 | Auckland | MWEL K06 | 2024-11-13 | 45609.6264 | 2024-11-13 | 45609.7424 | 0.05505 | 0.00046486 | 291 | 34461 | Unplanned | Third party interference
2406 |  | 36642 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-11-13 | 45609.6674 | 2024-11-14 | 45610.2812 | 0.057045 | 0.00046165 | 237 | 35710 | Unplanned | Vegetation
2407 |  | 36643 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-11-13 | 45609.2715 | 2024-11-13 | 45609.9028 | 0.0014521 | 1.597e-06 | 1 | 909 | Unplanned | Defective equipment
2408 |  | 36644 | TRIA K02 - K02 SOUTH | Northern | TRIA K02 | 2024-11-13 | 45609.875 | 2024-11-13 | 45609.9736 | 0.0011342 | 7.987e-06 | 5 | 710 | Planned | Planned
2409 |  | 36645 | GHIT K02 - K02 ORWELL RD | Northern | GHIT K02 | 2024-11-13 | 45609.8889 | 2024-11-14 | 45610.1562 | 0.0033067 | 4.7924e-05 | 30 | 2070 | Unplanned | Third party interference
2410 |  | 36646 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-11-13 | 45609.9799 | 2024-11-14 | 45610.141 | 0.10377 | 0.00044729 | 280 | 64960 | Planned | Planned
2411 |  | 36647 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-11-13 | 45609.9688 | 2024-11-14 | 45610.4618 | 0.0079394 | 1.1182e-05 | 7 | 4970 | Unplanned | Third party interference
2412 |  | 36648 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-11-14 | 45610.3333 | 2024-11-14 | 45610.7507 | 0.010459 | 0.0001262 | 43 | 6547 | Planned | Planned
2413 |  | 36649 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-11-14 | 45610.3958 | 2024-11-14 | 45610.6167 | 0.03048 | 9.5846e-05 | 60 | 19080 | Planned | Planned
2414 |  | 36650 | BAIR K07 - K07 MANUKAU TECH | Auckland | BAIR K07 | 2024-11-14 | 45610.4479 | 2024-11-14 | 45610.7951 | 0.035542 | 0.00010543 | 65 | 22249 | Unplanned | Defective equipment
2415 |  | 36650 | BAIR K07 - K07 MANUKAU TECH | Auckland | BAIR K13 | 2024-11-14 | 45610.4479 | 2024-11-14 | 45610.7951 | 0.29753 | 0.004147 | 2596 | 186255 | Unplanned | Defective equipment
2416 |  | 36651 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2024-11-14 | 45610.6236 | 2024-11-14 | 45610.7972 | 0.093451 | 0.00037381 | 234 | 58500 | Unplanned | Defective equipment
2417 |  | 36652 | SHOW K07 - K07 NICHOLAS RD | Auckland | SHOW K07 | 2024-11-14 | 45610.4201 | 2024-11-15 | 45611.5646 | 0.027182 | 0.00014856 | 93 | 17016 | Planned | Planned
2418 |  | 36653 | SAND K13 - K13 2 MAYN AVE | Auckland | SAND K13 | 2024-11-14 | 45610.7306 | 2024-11-14 | 45610.7549 | 0.0095049 | 0.00027157 | 170 | 5950 | Unplanned | Defective equipment
2419 |  | 36654 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-11-14 | 45610.7708 | 2024-11-15 | 45611.6597 | 0.0020447 | 1.597e-06 | 1 | 1280 | Unplanned | Defective equipment
2420 |  | 36655 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-11-14 | 45610.9583 | 2024-11-15 | 45611.0458 | 0.030192 | 0.00023962 | 150 | 18900 | Planned | Planned
2421 |  | 36657 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-11-15 | 45611.2368 | 2024-11-15 | 45611.3604 | 0.044628 | 0.00059106 | 370 | 27937 | Unplanned | Vegetation
2422 |  | 36659 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-15 | 45611.3354 | 2024-11-15 | 45611.5062 | 0.012182 | 4.9519e-05 | 31 | 7626 | Planned | Planned
2423 |  | 36660 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-15 | 45611.3604 | 2024-11-15 | 45611.6486 | 0.11469 | 0.00027636 | 173 | 71795 | Planned | Planned
2424 |  | 36661 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-11-15 | 45611.375 | 2024-11-15 | 45611.8056 | 0.02931 | 4.7926e-05 | 30 | 18348 | Planned | Planned
2425 |  | 36662 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-15 | 45611.3868 | 2024-11-15 | 45611.6389 | 0.0017396 | 4.792e-06 | 3 | 1089 | Planned | Planned
2426 |  | 36663 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-11-15 | 45611.4563 | 2024-11-15 | 45611.5069 | 0.018075 | 0.0002476 | 155 | 11315 | Unplanned | Vegetation
2427 |  | 36664 | ORAK K01 - K01 KEMPTHORNE CRES | Auckland | ORAK K01 | 2024-11-15 | 45611.4903 | 2024-11-15 | 45611.6028 | 0.11985 | 0.00074442 | 466 | 75026 | Unplanned | Vegetation
2428 |  | 36664 | ORAK K01 - K01 KEMPTHORNE CRES | Auckland | ORAK K13 | 2024-11-15 | 45611.4903 | 2024-11-15 | 45611.6028 | 0.13897 | 0.00085784 | 537 | 86994 | Unplanned | Vegetation
2429 |  | 36667 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-11-15 | 45611.6278 | 2024-11-15 | 45611.7181 | 0.013291 | 0.00010224 | 64 | 8320 | Unplanned | Vegetation
2430 |  | 36668 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-11-15 | 45611.6285 | 2024-11-15 | 45611.7215 | 0.0021406 | 1.5973e-05 | 10 | 1340 | Unplanned | Cause unknown
2431 |  | 36669 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2024-11-15 | 45611.75 | 2024-11-15 | 45611.8264 | 0.022141 | 0.00020127 | 126 | 13860 | Unplanned | Vegetation
2432 |  | 36670 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-15 | 45611.7993 | 2024-11-16 | 45612.6465 | 0.046307 | 0.00036422 | 204 | 28988 | Unplanned | Vegetation
2433 |  | 36671 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-11-15 | 45611.9167 | 2024-11-15 | 45611.9618 | 0.0020767 | 3.1949e-05 | 20 | 1300 | Unplanned | Vegetation
2434 |  | 36672 | SAND K18 - K18 SANDRINGHAM RD EXTN - SOUTH | Auckland | SAND K18 | 2024-11-15 | 45611.9583 | 2024-11-16 | 45612.2806 | 0.18086 | 0.00038978 | 244 | 113216 | Planned | Planned
2435 |  | 36673 | ROCK K13 - K13 GREENPARK RD | Auckland | ROCK K13 | 2024-11-16 | 45612 | 2024-11-16 | 45612.2528 | 0.010467 | 2.8753e-05 | 18 | 6552 | Planned | Planned
2436 |  | 36674 | HOBV K10 - K10 OREIL AVENUE | Northern | HOBV K10 | 2024-11-16 | 45612.1208 | 2024-11-16 | 45612.1674 | 0.043775 | 0.00065336 | 409 | 27403 | Unplanned | Cause unknown
2437 |  | 36675 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-11-16 | 45612.1465 | 2024-11-16 | 45612.2444 | 0.0040544 | 2.8754e-05 | 18 | 2538 | Unplanned | Cause unknown
2438 |  | 36677 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-11-16 | 45612.3542 | 2024-11-16 | 45612.7014 | 0.10064 | 0.00020127 | 126 | 63000 | Planned | Planned
2439 |  | 36678 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2024-11-16 | 45612.3333 | 2024-11-16 | 45612.5521 | 0.0005032 | 1.597e-06 | 1 | 315 | Planned | Planned
2440 |  | 36679 | WIRI K10 - K10 WIRI STATION RD WEST | Auckland | WIRI K10 | 2024-11-16 | 45612.3333 | 2024-11-16 | 45612.5903 | 0.0088659 | 2.3962e-05 | 15 | 5550 | Planned | Planned
2441 |  | 36680 | NLYN K08 - K08 TOTARA AVENUE | Northern | NLYN K08 | 2024-11-16 | 45612.3757 | 2024-11-16 | 45612.6028 | 0.0026118 | 7.987e-06 | 5 | 1635 | Planned | Planned
2442 |  | 36681 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-11-16 | 45612.3958 | 2024-11-16 | 45612.6583 | 0.054346 | 0.00014377 | 90 | 34020 | Planned | Planned
2443 |  | 36682 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2024-11-16 | 45612.3514 | 2024-11-16 | 45612.4861 | 0.017975 | 9.2653e-05 | 58 | 11252 | Unplanned | Defective equipment
2444 |  | 36684 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-11-17 | 45613.0931 | 2024-11-17 | 45613.3778 | 0.045192 | 0.00011022 | 69 | 28290 | Unplanned | Third party interference
2445 |  | 36685 | OTAR K07 - K07 BOTANY SOUTH | Auckland | OTAR K07 | 2024-11-17 | 45613.3333 | 2024-11-17 | 45613.6389 | 0.0034186 | 7.988e-06 | 5 | 2140 | Planned | Planned
2446 |  | 36686 | MNAB K33 - K33 GAVIN STREET EAST | Auckland | MNAB K33 | 2024-11-17 | 45613.375 | 2024-11-17 | 45613.4583 | 0.00038339 | 3.195e-06 | 2 | 240 | Planned | Planned
2447 |  | 36687 | NSBT93C - WAIMAUKU P1028/P1027 - RIVERHEAD H03 (93C) | Northern | WAIM K06 | 2024-11-17 | 45613.8194 | 2024-11-18 | 45614.3472 | 0.0871 | 0.00013418 | 84 | 54524 | Planned | Planned
2448 |  | 36688 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-11-17 | 45613.9792 | 2024-11-18 | 45614.1403 | 0.017419 | 7.508e-05 | 47 | 10904 | Planned | Planned
2449 |  | 36689 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-11-18 | 45614.3583 | 2024-11-18 | 45614.5583 | 0.0023003 | 7.987e-06 | 5 | 1440 | Planned | Planned
2450 |  | 36690 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2024-11-18 | 45614.3958 | 2024-11-18 | 45614.6361 | 0.14094 | 0.00040735 | 255 | 88230 | Planned | Planned
2451 |  | 36691 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-11-18 | 45614.4694 | 2024-11-18 | 45614.5437 | 0.024455 | 0.00037859 | 237 | 15309 | Unplanned | Cause unknown
2452 |  | 36692 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-11-18 | 45614.6146 | 2024-11-18 | 45614.6403 | 0.00023642 | 6.39e-06 | 4 | 148 | Unplanned | Defective equipment
2453 |  | 36693 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-11-18 | 45614.65 | 2024-11-19 | 45615.1208 | 0.064299 | 0.00024921 | 99 | 40251 | Unplanned | Third party interference
2454 |  | 36694 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-11-18 | 45614.8271 | 2024-11-19 | 45615.0542 | 0.04396 | 0.0003722 | 233 | 27519 | Unplanned | Vegetation
2455 |  | 36695 | MANL K01 - K01 ARMY BAY | Northern | MANL K01 | 2024-11-18 | 45614.9326 | 2024-11-19 | 45615.0819 | 0.12124 | 0.0005639 | 353 | 75895 | Unplanned | Defective equipment
2456 |  | 36696 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-11-18 | 45614.9583 | 2024-11-19 | 45615.0451 | 0.018171 | 0.00014537 | 91 | 11375 | Planned | Planned
2457 |  | 36697 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-11-19 | 45615.0833 | 2024-11-19 | 45615.1701 | 0.014776 | 0.00011821 | 74 | 9250 | Planned | Planned
2458 |  | 36698 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-19 | 45615.2083 | 2024-11-19 | 45615.6708 | 0.088603 | 0.0012173 | 762 | 55465 | Planned | Planned
2459 |  | 36699 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-11-19 | 45615.2188 | 2024-11-19 | 45615.2903 | 0.0029617 | 2.8754e-05 | 18 | 1854 | Planned | Planned
2460 |  | 36700 | BIRK K12 - K12 STANLEY ROAD | Northern | BIRK K12 | 2024-11-19 | 45615.3542 | 2024-11-19 | 45615.7333 | 0.23201 | 0.00042492 | 266 | 145236 | Planned | Planned
2461 |  | 36701 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2024-11-19 | 45615.3535 | 2024-11-19 | 45615.6889 | 0.21912 | 0.00070767 | 363 | 137169 | Planned | Planned
2462 |  | 36702 | PAKU K09 - K09 UDYS RD | Auckland | PAKU K09 | 2024-11-19 | 45615.4194 | 2024-11-19 | 45615.5826 | 0.019146 | 8.147e-05 | 51 | 11985 | Planned | Planned
2463 |  | 36703 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-11-19 | 45615.7701 | 2024-11-19 | 45615.8528 | 0.0034218 | 2.8754e-05 | 18 | 2142 | Planned | Planned
2464 |  | 36704 | MWES K10 - K10 KIWI HARVEST | Auckland | MWES K10 | 2024-11-19 | 45615.9167 | 2024-11-20 | 45616.0021 | 0.00019649 | 1.597e-06 | 1 | 123 | Planned | Planned
2465 |  | 36705 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-11-19 | 45615.9792 | 2024-11-20 | 45616.1715 | 0.073081 | 0.00058148 | 262 | 45748 | Planned | Planned
2466 |  | 36706 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-11-20 | 45616.1201 | 2024-11-20 | 45616.1681 | 0.01315 | 0.00051758 | 324 | 8232 | Unplanned | Wildlife
2467 |  | 36708 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-11-20 | 45616.4097 | 2024-11-20 | 45616.6236 | 0.0044282 | 1.4377e-05 | 9 | 2772 | Planned | Planned
2468 |  | 36709 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-20 | 45616.3604 | 2024-11-20 | 45616.4306 | 0.00064537 | 6.389e-06 | 4 | 404 | Unplanned | Cause unknown
2469 |  | 36710 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-20 | 45616.7375 | 2024-11-21 | 45617.0938 | 0.0024585 | 4.792e-06 | 3 | 1539 | Unplanned | Defective equipment
2470 |  | 36712 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2024-11-20 | 45616.8542 | 2024-11-21 | 45617.2319 | 0.27118 | 0.00054793 | 343 | 169760 | Planned | Planned
2471 |  | 36713 | DRIV K06 - K06 EVE'S EPSOM | Auckland | DRIV K06 | 2024-11-20 | 45616.9792 | 2024-11-21 | 45617.1813 | 0.085999 | 0.00029553 | 185 | 53835 | Planned | Planned
2472 |  | 36713 | DRIV K06 - K06 EVE'S EPSOM | Auckland | NEWM K01 | 2024-11-20 | 45616.9792 | 2024-11-21 | 45617.1813 | 0.025165 | 9.425e-05 | 59 | 15753 | Planned | Planned
2473 |  | 36714 | WGAT K10 - K10 TAWHIA | Northern | WGAT K10 | 2024-11-20 | 45616.9583 | 2024-11-21 | 45617.0715 | 0.00026039 | 1.597e-06 | 1 | 163 | Planned | Planned
2474 |  | 36715 | MANL K01 - K01 ARMY BAY | Northern | MANL K01 | 2024-11-21 | 45617.3333 | 2024-11-21 | 45617.7021 | 0.16032 | 0.00030192 | 189 | 100359 | Planned | Planned
2475 |  | 36716 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2024-11-21 | 45617.3451 | 2024-11-21 | 45617.4222 | 0.0019505 | 1.7572e-05 | 11 | 1221 | Unplanned | Cause unknown
2476 |  | 36717 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-11-21 | 45617.6076 | 2024-11-21 | 45617.6632 | 0.00025559 | 3.195e-06 | 2 | 160 | Unplanned | Cause unknown
2477 |  | 36718 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-11-21 | 45617.8368 | 2024-11-21 | 45617.8736 | 0.0032173 | 6.0703e-05 | 38 | 2014 | Unplanned | Defective equipment
2478 |  | 36719 | KING K02 - K02 KINGSLAND AVE | Auckland | KING K02 | 2024-11-22 | 45618.0417 | 2024-11-22 | 45618.1826 | 0.083365 | 0.00041534 | 260 | 52186 | Planned | Planned
2479 |  | 36720 | RANU K08 - K08 MIHINI ROAD | Northern | RANU K08 | 2024-11-21 | 45617.9167 | 2024-11-22 | 45618.0229 | 0.0017109 | 1.1182e-05 | 7 | 1071 | Planned | Planned
2480 |  | 36721 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2024-11-22 | 45618.0417 | 2024-11-22 | 45618.1764 | 0.059847 | 0.00032588 | 204 | 37464 | Planned | Planned
2481 |  | 36722 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-22 | 45618.3542 | 2024-11-22 | 45618.6486 | 0.015578 | 3.674e-05 | 23 | 9752 | Planned | Planned
2482 |  | 36723 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2024-11-22 | 45618.4167 | 2024-11-22 | 45618.6194 | 0.014927 | 5.1119e-05 | 32 | 9344 | Planned | Planned
2483 |  | 36724 | OTAR K15 - K15 NZ WINES & SPIRITS | Auckland | OTAR K15 | 2024-11-22 | 45618.6056 | 2024-11-22 | 45618.7924 | 0.0017189 | 6.39e-06 | 4 | 1076 | Unplanned | Defective equipment
2484 |  | 36725 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-11-22 | 45618.791 | 2024-11-22 | 45618.8389 | 0.00011022 | 1.597e-06 | 1 | 69 | Unplanned | Defective equipment
2485 |  | 36726 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2024-11-22 | 45618.9167 | 2024-11-23 | 45619.3021 | 0.33181 | 0.00063739 | 399 | 207711 | Planned | Planned
2486 |  | 36727 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-11-23 | 45619.0347 | 2024-11-23 | 45619.1507 | 0.00026678 | 1.597e-06 | 1 | 167 | Unplanned | Defective equipment
2487 |  | 36728 | SABU K02 - K02 HEPBURN RD | Northern | SABU K02 | 2024-11-23 | 45619.3347 | 2024-11-23 | 45619.5944 | 0.0023898 | 6.39e-06 | 4 | 1496 | Planned | Planned
2488 |  | 36729 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-11-23 | 45619.3403 | 2024-11-23 | 45619.5014 | 0.09345 | 0.001409 | 882 | 58499 | Unplanned | Wildlife
2489 |  | 36731 | HILL K03 - K03 19 HERD RD | Auckland | HILL K03 | 2024-11-23 | 45619.4028 | 2024-11-23 | 45619.7778 | 0.19056 | 0.00036103 | 226 | 119290 | Planned | Planned
2490 |  | 36732 | MANU K04 - K04 CENTRE WEYMOUTH RD VIA LS | Auckland | MANU K04 | 2024-11-23 | 45619.4583 | 2024-11-23 | 45619.6736 | 0.12776 | 0.00041214 | 258 | 79980 | Unplanned | Third party interference
2491 |  | 36733 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-11-23 | 45619.5833 | 2024-11-23 | 45619.5903 | 0.0001917 | 1.917e-05 | 12 | 120 | Unplanned | Other Cause | Outage caused by Tap Operation
2492 |  | 36734 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-11-23 | 45619.6174 | 2024-11-23 | 45619.6868 | 0.022358 | 0.00027637 | 173 | 13996 | Unplanned | Vegetation
2493 |  | 36735 | WIRI K22 - K22 227 ROSCOMMON RD | Auckland | WIRI K22 | 2024-11-24 | 45620.3549 | 2024-11-24 | 45620.6653 | 0.0035703 | 7.987e-06 | 5 | 2235 | Planned | Planned
2494 |  | 36738 | RANU K06 - K06 METCALFE ROAD | Northern | RANU K06 | 2024-11-24 | 45620.5014 | 2024-11-24 | 45620.8618 | 0.17659 | 0.00034026 | 213 | 110547 | Unplanned | Third party interference
2495 |  | 36739 | VICT K24 - K24 BROOKE BUILDING VIA LS | Auckland | VICT K24 | 2024-11-24 | 45620.9792 | 2024-11-25 | 45621.1667 | 0.035799 | 0.00013259 | 83 | 22410 | Planned | Planned
2496 |  | 36740 | SHEL K06 - K06 RIDDELL RD EAST | Auckland | SHEL K06 | 2024-11-25 | 45621.0417 | 2024-11-25 | 45621.1681 | 0.050298 | 0.00027636 | 173 | 31486 | Planned | Planned
2497 |  | 36742 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-11-25 | 45621.0069 | 2024-11-25 | 45621.1306 | 0.014502 | 8.147e-05 | 51 | 9078 | Unplanned | Defective equipment
2498 |  | 36744 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-11-25 | 45621.3785 | 2024-11-25 | 45621.7194 | 0.0039218 | 7.987e-06 | 5 | 2455 | Planned | Planned
2499 |  | 36745 | TATA K07 - K07 JAEMONT AVENUE | Northern | TATA K07 | 2024-11-25 | 45621.3958 | 2024-11-25 | 45621.7104 | 0.058616 | 0.00012939 | 81 | 36693 | Planned | Planned
2500 |  | 36746 | QUAY J04 - J04 ZURICH HOUSE | Auckland | QUAY J04 | 2024-11-25 | 45621.3083 | 2024-11-25 | 45621.5444 | 0.00054314 | 1.597e-06 | 1 | 340 | Unplanned | Cause unknown
2501 |  | 36747 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-11-25 | 45621.2514 | 2024-11-25 | 45621.3708 | 0.0049457 | 2.8753e-05 | 18 | 3096 | Unplanned | Cause unknown
2502 |  | 36749 | SHEL K05 - K05 RIDDELL RD WEST | Auckland | SHEL K05 | 2024-11-25 | 45621.4174 | 2024-11-25 | 45621.5938 | 0.025968 | 0.00010224 | 64 | 16256 | Planned | Planned
2503 |  | 36750 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-11-25 | 45621.3812 | 2024-11-26 | 45622.016 | 0.074464 | 8.147e-05 | 51 | 46614 | Unplanned | Defective equipment
2504 |  | 36754 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-11-25 | 45621.8736 | 2024-11-25 | 45621.9674 | 0.0015096 | 1.1182e-05 | 7 | 945 | Unplanned | Wildlife
2505 |  | 36755 | MWEL K03 - K03 BRISCOES | Auckland | MWEL K03 | 2024-11-26 | 45622.0417 | 2024-11-26 | 45622.1153 | 0.021674 | 0.00020447 | 128 | 13568 | Unplanned | Defective equipment
2506 |  | 36756 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-26 | 45622.2111 | 2024-11-26 | 45622.7194 | 0.041451 | 0.0023038 | 721 | 25948 | Planned | Planned
2507 |  | 36757 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-26 | 45622.3646 | 2024-11-26 | 45622.7146 | 0.078097 | 0.00015495 | 97 | 48888 | Planned | Planned
2508 |  | 36758 | CLEN K11 - K11 SHARLAND | Auckland | CLEN K11 | 2024-11-26 | 45622.2465 | 2024-11-26 | 45622.3625 | 0.016807 | 0.00010064 | 63 | 10521 | Unplanned | Cause unknown
2509 |  | 36759 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-11-26 | 45622.7153 | 2024-11-26 | 45622.9514 | 0.0092333 | 2.7157e-05 | 17 | 5780 | Planned | Planned
2510 |  | 36760 | FREE K20 - K20 FRANKLIN RD 44 | Auckland | FREE K65 | 2024-11-26 | 45622.875 | 2024-11-27 | 45623.0167 | 0.039106 | 0.0001917 | 120 | 24480 | Planned | Planned
2511 |  | 36761 | NEWT K24 - K24 EXMOUTH ST 25 | Auckland | NEWT K24 | 2024-11-27 | 45623.3958 | 2024-11-27 | 45623.691 | 0.098443 | 0.00023163 | 145 | 61625 | Planned | Planned
2512 |  | 36764 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2024-11-27 | 45623.3354 | 2024-11-27 | 45623.7069 | 0.21793 | 0.00040735 | 255 | 136425 | Planned | Planned
2513 |  | 36765 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-11-27 | 45623.3757 | 2024-11-27 | 45623.6951 | 0.046294 | 0.00010064 | 63 | 28980 | Planned | Planned
2514 |  | 36766 | ATKI K05 - K05 WEST LYNN | Northern | ATKI K05 | 2024-11-27 | 45623.441 | 2024-11-27 | 45623.4736 | 0.022599 | 0.00048084 | 301 | 14147 | Unplanned | Cause unknown
2515 |  | 36767 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-11-27 | 45623.534 | 2024-11-27 | 45623.709 | 0.0032205 | 1.2779e-05 | 8 | 2016 | Unplanned | Defective equipment
2516 |  | 36768 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2024-11-27 | 45623.7306 | 2024-11-28 | 45624.1556 | 0.019553 | 3.1948e-05 | 20 | 12240 | Planned | Planned
2517 |  | 36769 | KEEL K13 - K13 SWANSON ROAD | Northern | KEEL K13 | 2024-11-27 | 45623.9167 | 2024-11-28 | 45624.0882 | 0.014205 | 5.7509e-05 | 36 | 8892 | Planned | Planned
2518 |  | 36770 | JAME K10 - K10 HOGANS ROAD | Northern | JAME K10 | 2024-11-27 | 45623.9187 | 2024-11-28 | 45624.8674 | 0.066093 | 0.00025879 | 139 | 41374 | Planned | Planned
2519 |  | 36771 | NEWT K24 - K24 EXMOUTH ST 25 | Auckland | NEWT K24 | 2024-11-27 | 45623.9167 | 2024-11-28 | 45624.1 | 0.021016 | 0.00016614 | 52 | 13156 | Planned | Planned
2520 |  | 36772 | MWES K10 - K10 KIWI HARVEST | Auckland | MWES K10 | 2024-11-27 | 45623.9174 | 2024-11-28 | 45624.0729 | 0.00035783 | 1.597e-06 | 1 | 224 | Planned | Planned
2521 |  | 36773 | ROSE K02 - K02 ROSEBANK RD SOUTH | Auckland | ROSE K02 | 2024-11-27 | 45623.9583 | 2024-11-28 | 45624.1562 | 0.047804 | 0.00016773 | 105 | 29925 | Planned | Planned
2522 |  | 36774 | MANU K07 - K07 HALVER RD | Auckland | MANU K07 | 2024-11-28 | 45624.2083 | 2024-11-28 | 45624.5347 | 0.007024 | 0.0001917 | 120 | 4397 | Planned | Planned
2523 |  | 36776 | MANU K03 - K03 COXHEAD RD | Auckland | MANU K03 | 2024-11-28 | 45624.3694 | 2024-11-28 | 45624.4139 | 0.20309 | 0.0032445 | 2031 | 127134 | Unplanned | Wildlife
2524 |  | 36777 | MARA K10 - K10 OMANA BEACH RD | Auckland | MARA K10 | 2024-11-28 | 45624.4181 | 2024-11-28 | 45624.6931 | 0.050608 | 0.00012779 | 80 | 31680 | Planned | Planned
2525 |  | 36778 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2024-11-28 | 45624.334 | 2024-11-28 | 45624.6736 | 0.012499 | 2.5559e-05 | 16 | 7824 | Planned | Planned
2526 |  | 36779 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-28 | 45624.3549 | 2024-11-28 | 45624.7188 | 0.037668 | 7.1883e-05 | 45 | 23580 | Planned | Planned
2527 |  | 36780 | KING K01 - K01 DOMINION RD | Auckland | KING K01 | 2024-11-28 | 45624.3958 | 2024-11-28 | 45624.6528 | 0.036646 | 9.9043e-05 | 62 | 22940 | Planned | Planned
2528 |  | 36781 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-11-28 | 45624.375 | 2024-11-28 | 45624.6993 | 0.060331 | 0.0001294 | 81 | 37767 | Planned | Planned
2529 |  | 36782 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-11-28 | 45624.6056 | 2024-11-28 | 45624.6132 | 0.0017396 | 0.00015814 | 99 | 1089 | Unplanned | Human error
2530 |  | 36783 | WIRI K15 - K15 KEITH HAY DR | Auckland | WIRI K15 | 2024-11-28 | 45624.6208 | 2024-11-28 | 45624.8 | 0.013189 | 5.1119e-05 | 32 | 8256 | Unplanned | Third party interference
2531 |  | 36784 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2024-11-28 | 45624.9792 | 2024-11-29 | 45625.0903 | 0.014824 | 9.2653e-05 | 58 | 9280 | Planned | Planned
2532 |  | 36785 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-11-29 | 45625.2083 | 2024-11-29 | 45625.7792 | 0.034248 | 0.0023004 | 720 | 21439 | Planned | Planned
2533 |  | 36786 | DRIV K16 - K16 MANUKAU RD | Auckland | DRIV K16 | 2024-11-29 | 45625.05 | 2024-11-29 | 45625.1257 | 0.032909 | 0.00030192 | 189 | 20601 | Planned | Planned
2534 |  | 36787 | TPAP K11 - K11 NZ RIBBON | Auckland | TPAP K11 | 2024-11-29 | 45625.2292 | 2024-12-02 | 45628.3056 | 0.00017572 | 6.39e-06 | 2 | 110 | Planned | Planned
2535 |  | 36789 | ROCK K10 - K10 ROCKFIELD RD 136 | Auckland | ROCK K10 | 2024-11-29 | 45625.3861 | 2024-12-04 | 45630.6715 | 0.012158 | 1.597e-06 | 1 | 7611 | Unplanned | Third party interference
2536 |  | 36790 | OREW K10 - K10 HATFIELDS | Northern | OREW K10 | 2024-11-29 | 45625.3778 | 2024-11-29 | 45625.5028 | 0.026454 | 0.00014697 | 92 | 16560 | Planned | Planned
2537 |  | 36791 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-29 | 45625.5625 | 2024-11-29 | 45625.6285 | 0.0015176 | 1.5974e-05 | 10 | 950 | Planned | Planned
2538 |  | 36792 | SWAN K02 - K02 BIRDWOOD | Northern | SWAN K02 | 2024-11-29 | 45625.7188 | 2024-11-29 | 45625.7396 | 0.0017253 | 5.7508e-05 | 36 | 1080 | Unplanned | Other Cause | Outage caused by Tap Operation
2539 |  | 36793 | ROCK K09 - K09 604 GREAT SOUTH RD | Auckland | DRIV K06 | 2024-11-29 | 45625.8187 | 2024-11-29 | 45625.9444 | 0.0010719 | 0.0010719 | 671 | 671 | Unplanned | Defective equipment
2540 |  | 36793 | ROCK K09 - K09 604 GREAT SOUTH RD | Auckland | ROCK K09 | 2024-11-29 | 45625.8187 | 2024-11-29 | 45625.9444 | 0.15092 | 0.0016662 | 1043 | 94475 | Unplanned | Defective equipment
2541 |  | 36794 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-11-29 | 45625.8313 | 2024-11-29 | 45625.8646 | 0.00076678 | 1.5974e-05 | 10 | 480 | Unplanned | Cause unknown
2542 |  | 36795 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-11-29 | 45625.8875 | 2024-11-29 | 45625.9639 | 0.00070288 | 6.389e-06 | 4 | 440 | Unplanned | Cause unknown
2543 |  | 36797 | MWES K02 - K02 ORUARANGI RD | Auckland | MWES K02 | 2024-11-30 | 45626.266 | 2024-11-30 | 45626.4062 | 0.00064537 | 3.194e-06 | 2 | 404 | Unplanned | Wildlife
2544 |  | 36798 | BAIR K02 - K02 KERWYN AVE | Auckland | BAIR K02 | 2024-11-30 | 45626.35 | 2024-11-30 | 45626.5535 | 0.00046806 | 1.597e-06 | 1 | 293 | Planned | Planned
2545 |  | 36799 | WGAT K11 - K11 HOLMES | Northern | WGAT K11 | 2024-11-30 | 45626.3549 | 2024-11-30 | 45626.7535 | 0.10453 | 0.00018211 | 114 | 65436 | Planned | Planned
2546 |  | 36800 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-11-30 | 45626.6319 | 2024-11-30 | 45626.6924 | 0.037869 | 0.00050002 | 313 | 23706 | Unplanned | Cause unknown
2547 |  | 36801 | TAKA K19 - K19 PORCHESTER RD | Auckland | TAKA K19 | 2024-11-30 | 45626.7299 | 2024-11-30 | 45626.809 | 0.0050991 | 4.4726e-05 | 28 | 3192 | Planned | Planned
2548 |  | 36802 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-11-30 | 45626.7472 | 2024-11-30 | 45626.9132 | 0.00076359 | 3.194e-06 | 2 | 478 | Unplanned | Vegetation
2549 |  | 36803 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-12-01 | 45627.1646 | 2024-12-01 | 45627.4083 | 0.097111 | 0.0010048 | 533 | 60791 | Unplanned | Vegetation
2550 |  | 36804 | ROSE K08 - K08 HONAN PL PHIPPS ROCOL | Auckland | ROSE K08 | 2024-12-01 | 45627.2625 | 2024-12-01 | 45627.4243 | 0.26684 | 0.003393 | 1282 | 167038 | Unplanned | Third party interference
2551 |  | 36805 | MKAU K12 - K12 LAMBIE DRIVE | Auckland | MKAU K12 | 2024-12-01 | 45627.3542 | 2024-12-01 | 45627.5951 | 0.0038802 | 1.1182e-05 | 7 | 2429 | Planned | Planned
2552 |  | 36807 | BAIR K09 - K09 CARTER HOLT | Auckland | BAIR K09 | 2024-12-01 | 45627.6708 | 2024-12-02 | 45628.7917 | 0.012891 | 7.987e-06 | 5 | 8070 | Unplanned | Third party interference
2553 |  | 36808 | HPOI K07 - K07 POTTERY CRES | Northern | HPOI K07 | 2024-12-01 | 45627.7583 | 2024-12-01 | 45627.8215 | 0.052496 | 0.0011023 | 690 | 32862 | Unplanned | Cause unknown
2554 |  | 36809 | WAIK K02 - K02 ROSIER ROAD | Northern | WAIK K02 | 2024-12-01 | 45627.759 | 2024-12-01 | 45627.8625 | 0.076643 | 0.00051438 | 322 | 47978 | Unplanned | Defective equipment
2555 |  | 36810 | TPAP K08 - K08 CHURCH ST WEST VIA LS | Auckland | TPAP K08 | 2024-12-01 | 45627.8056 | 2024-12-02 | 45628.2799 | 0.18472 | 0.00076678 | 311 | 115632 | Unplanned | Third party interference
2556 |  | 36811 | MKAU K27 - K27 CARTER HOLT (VIA LST1) | Auckland | MKAU K27 | 2024-12-01 | 45627.8868 | 2024-12-01 | 45627.9306 | 0.0013083 | 2.0767e-05 | 13 | 819 | Unplanned | Third party interference
2557 |  | 36813 | WIRI K13 - K13 117 KERRS RD | Auckland | WIRI K13 | 2024-12-02 | 45628.3368 | 2024-12-02 | 45628.391 | 0.0040064 | 8.1467e-05 | 51 | 2508 | Unplanned | Defective equipment
2558 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K02 | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 0.013217 | 0.00062944 | 394 | 8274 | Unplanned | Vegetation
2559 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K03 | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 0.011246 | 0.00051115 | 320 | 7040 | Unplanned | Vegetation
2560 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K05 | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 0.044862 | 0.0013594 | 851 | 28083 | Unplanned | Vegetation
2561 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K06 | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 0.014856 | 0.00059427 | 372 | 9300 | Unplanned | Vegetation
2562 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K08 | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 0.038358 | 0.0010655 | 667 | 24012 | Unplanned | Vegetation
2563 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K09 | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 0.16116 | 0.0033004 | 2066 | 100884 | Unplanned | Vegetation
2564 |  | 36814 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM LS | 2024-12-02 | 45628.4535 | 2024-12-02 | 45628.5139 | 5.7508e-05 | 1.6e-06 | 1 | 36 | Unplanned | Vegetation
2565 |  | 36815 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-12-02 | 45628.4951 | 2024-12-02 | 45628.6611 | 0.013363 | 5.5911e-05 | 35 | 8365 | Unplanned | Defective equipment
2566 |  | 36816 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2024-12-02 | 45628.6847 | 2024-12-02 | 45628.7486 | 0.0011757 | 1.278e-05 | 8 | 736 | Unplanned | Defective equipment
2567 |  | 36817 | GHIT K07 - K07 BLACKS RD | Northern | GHIT K07 | 2024-12-02 | 45628.8569 | 2024-12-02 | 45628.909 | 0.00023962 | 3.195e-06 | 2 | 150 | Unplanned | Cause unknown
2568 |  | 36818 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2024-12-02 | 45628.9646 | 2024-12-03 | 45629.075 | 0.070357 | 0.0004425 | 277 | 44043 | Planned | Planned
2569 |  | 36819 | REMU K07 - K07 GREENLANE RD EAST | Auckland | REMU K07 | 2024-12-02 | 45628.9625 | 2024-12-03 | 45629.2361 | 0.10133 | 0.00025719 | 161 | 63434 | Planned | Planned
2570 |  | 36820 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-12-03 | 45629.1979 | 2024-12-03 | 45629.8285 | 0.0073898 | 5.751e-05 | 18 | 4626 | Planned | Planned
2571 |  | 36821 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-12-03 | 45629.2097 | 2024-12-03 | 45629.7188 | 0.035604 | 0.0016502 | 720 | 22288 | Planned | Planned
2572 |  | 36822 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-12-03 | 45629.25 | 2024-12-03 | 45629.9104 | 0.003048 | 5.751e-05 | 18 | 1908 | Planned | Planned
2573 |  | 36823 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-03 | 45629.3333 | 2024-12-03 | 45629.4083 | 0.033642 | 0.0003115 | 195 | 21060 | Unplanned | Wildlife
2574 |  | 36824 | MKAU K12 - K12 LAMBIE DRIVE | Auckland | MKAU K12 | 2024-12-03 | 45629.4319 | 2024-12-03 | 45629.8528 | 0.11423 | 0.0001885 | 118 | 71508 | Unplanned | Third party interference
2575 |  | 36826 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-12-03 | 45629.5632 | 2024-12-03 | 45629.5667 | 8.786e-05 | 1.7572e-05 | 11 | 55 | Unplanned | Other Cause | Outage caused by Tap Operation
2576 |  | 36827 | PAPA K13 - K13 BATES ST | Auckland | PAPA K13 | 2024-12-03 | 45629.6646 | 2024-12-03 | 45629.8125 | 0.00068052 | 3.195e-06 | 2 | 426 | Unplanned | Defective equipment
2577 |  | 36828 | WAIA K05 - K05 CARLISE ROAD | Northern | WAIA K05 | 2024-12-03 | 45629.7597 | 2024-12-03 | 45629.8035 | 0.018112 | 0.0004409 | 276 | 11338 | Unplanned | Defective equipment
2578 |  | 36829 | HPOI K07 - K07 POTTERY CRES | Northern | HPOI K07 | 2024-12-03 | 45629.7583 | 2024-12-05 | 45631.0597 | 0.028184 | 0.00014377 | 84 | 17643 | Unplanned | Third party interference
2579 |  | 36830 | NLYN K01 - K01 ARAWA ST | Northern | NLYN K01 | 2024-12-03 | 45629.7646 | 2024-12-05 | 45631.5597 | 0.0041294 | 1.597e-06 | 1 | 2585 | Unplanned | Cause unknown
2580 |  | 36831 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2024-12-04 | 45630.25 | 2024-12-04 | 45630.6715 | 0.2383 | 0.00085784 | 447 | 149172 | Planned | Planned
2581 |  | 36832 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-12-04 | 45630.234 | 2024-12-04 | 45630.3271 | 0.00042812 | 3.195e-06 | 2 | 268 | Unplanned | Cause unknown
2582 |  | 36833 | ROSE K01 - K01 GLUCINA SMELTERS | Auckland | ROSE K01 | 2024-12-04 | 45630.2556 | 2024-12-04 | 45630.5 | 0.0016869 | 4.792e-06 | 3 | 1056 | Unplanned | Defective equipment
2583 |  | 36834 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2024-12-04 | 45630.3542 | 2024-12-04 | 45630.5514 | 0.066691 | 0.00023482 | 147 | 41748 | Planned | Planned
2584 |  | 36836 | ATKI K09 - K09 KAURILANDS RD | Northern | ATKI K09 | 2024-12-04 | 45630.3542 | 2024-12-04 | 45630.7264 | 0.087336 | 0.00016294 | 102 | 54672 | Planned | Planned
2585 |  | 36837 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-12-04 | 45630.3958 | 2024-12-04 | 45630.6312 | 0.14405 | 0.00042492 | 266 | 90174 | Planned | Planned
2586 |  | 36838 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-12-04 | 45630.6576 | 2024-12-05 | 45631.0139 | 0.064759 | 0.00077318 | 484 | 40539 | Unplanned | Third party interference
2587 |  | 36839 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2024-12-04 | 45630.7007 | 2024-12-04 | 45630.7028 | 4.7924e-05 | 1.5975e-05 | 10 | 30 | Unplanned | Other Cause | Outage caused by Tap Operation
2588 |  | 36840 | FORR K11 - K11 BLAKEBOROUGH DR + LS | Northern | FORR K11 | 2024-12-04 | 45630.7 | 2024-12-05 | 45631.0868 | 0.081605 | 0.000754 | 472 | 51084 | Unplanned | Defective equipment
2589 |  | 36841 | SAND K18 - K18 SANDRINGHAM RD EXTN - SOUTH | Auckland | SAND K18 | 2024-12-04 | 45630.9201 | 2024-12-05 | 45631.1007 | 0.039873 | 0.00015336 | 96 | 24960 | Planned | Planned
2590 |  | 36842 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-12-04 | 45630.9653 | 2024-12-05 | 45631.1736 | 0.001917 | 6.39e-06 | 4 | 1200 | Planned | Planned
2591 |  | 36844 | OTAR K07 - K07 BOTANY SOUTH | Auckland | OTAR K07 | 2024-12-04 | 45630.9625 | 2024-12-05 | 45631.1111 | 0.00068371 | 3.195e-06 | 2 | 428 | Unplanned | Defective equipment
2592 |  | 36845 | QUAY K04 - K04 TRANZ RAIL | Auckland | QUAY K04 | 2024-12-05 | 45631.2083 | 2024-12-05 | 45631.2229 | 0.0010399 | 4.9521e-05 | 31 | 651 | Planned | Planned
2593 |  | 36846 | HOBV K01 - K01 WESTPARK DRIVE | Northern | HOBV K01 | 2024-12-05 | 45631.3333 | 2024-12-05 | 45631.6965 | 0.035925 | 6.8691e-05 | 43 | 22489 | Planned | Planned
2594 |  | 36847 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-12-05 | 45631.3556 | 2024-12-05 | 45631.6979 | 0.063004 | 0.00012779 | 80 | 39440 | Planned | Planned
2595 |  | 36848 | MCEN K17 - K17 COURT TOWN CLOSE | Auckland | MCEN K17 | 2024-12-05 | 45631.375 | 2024-12-05 | 45631.8181 | 0.14269 | 0.00022364 | 140 | 89320 | Planned | Planned
2596 |  | 36849 | MCEN K11 - K11 MAHUNGA DRIVE | Auckland | MCEN K11 | 2024-12-05 | 45631.3785 | 2024-12-05 | 45631.4042 | 0.00011821 | 3.195e-06 | 2 | 74 | Planned | Planned
2597 |  | 36851 | HVAL K05 - K05 BORDER RD | Northern | HVAL K05 | 2024-12-05 | 45631.6431 | 2024-12-06 | 45632.8736 | 0.076036 | 0.00019649 | 97 | 47598 | Unplanned | Third party interference
2598 |  | 36852 | WIRI K11 - K11 100 PLUNKET AVE | Auckland | WIRI K11 | 2024-12-06 | 45632.0111 | 2024-12-06 | 45632.1819 | 0.01061 | 4.3132e-05 | 27 | 6642 | Planned | Planned
2599 |  | 36853 | NEWT K24 - K24 EXMOUTH ST 25 | Auckland | NEWT K24 | 2024-12-05 | 45631.9181 | 2024-12-06 | 45632.0389 | 0.014454 | 8.3068e-05 | 52 | 9048 | Planned | Planned
2600 |  | 36854 | WOOD K02 - K02 SEL PEACOCK DR | Northern | WOOD K02 | 2024-12-05 | 45631.9167 | 2024-12-06 | 45632.0333 | 0.020665 | 0.000123 | 77 | 12936 | Planned | Planned
2601 |  | 36855 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-12-06 | 45632.2097 | 2024-12-06 | 45632.716 | 0.025389 | 0.0023005 | 720 | 15893 | Planned | Planned
2602 |  | 36856 | SHEL K06 - K06 RIDDELL RD EAST | Auckland | SHEL K06 | 2024-12-06 | 45632.2264 | 2024-12-06 | 45632.4097 | 0.31954 | 0.0054953 | 1922 | 200029 | Unplanned | Defective equipment
2603 |  | 36858 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-12-06 | 45632.2153 | 2024-12-06 | 45632.2944 | 0.0036422 | 3.1947e-05 | 20 | 2280 | Unplanned | Cause unknown
2604 |  | 36859 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2024-12-06 | 45632.3542 | 2024-12-06 | 45632.6312 | 0.024221 | 6.0703e-05 | 38 | 15162 | Planned | Planned
2605 |  | 36860 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-12-06 | 45632.3542 | 2024-12-06 | 45632.6035 | 0.12789 | 0.00035623 | 223 | 80057 | Planned | Planned
2606 |  | 36861 | SHEL K05 - K05 RIDDELL RD WEST | Auckland | SHEL K05 | 2024-12-06 | 45632.4174 | 2024-12-06 | 45632.5215 | 0.015336 | 0.00010224 | 64 | 9600 | Planned | Planned
2607 |  | 36863 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-12-06 | 45632.4667 | 2024-12-06 | 45632.5417 | 0.010697 | 9.9037e-05 | 62 | 6696 | Unplanned | Cause unknown
2608 |  | 36864 | LIVE K19 - K19 67-69 SYMONDS ST VIA LS | Auckland | LIVE K19 | 2024-12-06 | 45632.375 | 2024-12-06 | 45632.5104 | 0.0059186 | 3.0352e-05 | 19 | 3705 | Planned | Planned
2609 |  | 36865 | SWAN K02 - K02 BIRDWOOD | Northern | SWAN K02 | 2024-12-06 | 45632.7847 | 2024-12-07 | 45633.191 | 0.057005 | 9.7445e-05 | 61 | 35685 | Unplanned | Defective equipment
2610 |  | 36866 | ONEH K12 - K12 - SELWYN ST SOUTH + LS | Auckland | ONEH K12 | 2024-12-07 | 45633.0007 | 2024-12-07 | 45633.225 | 0.060886 | 0.0001885 | 118 | 38114 | Planned | Planned
2611 |  | 36867 | HVAL K05 - K05 BORDER RD | Northern | HVAL K05 | 2024-12-07 | 45633.1243 | 2024-12-07 | 45633.184 | 0.012634 | 0.00015495 | 97 | 7909 | Unplanned | Defective equipment
2612 |  | 36868 | ECOA K08 - K08 LYONS AVENUE | Northern | ECOA K08 | 2024-12-07 | 45633.4076 | 2024-12-07 | 45633.4521 | 0.038237 | 0.00059745 | 374 | 23936 | Unplanned | Wildlife
2613 |  | 36869 | TPAP K17 - K17 PATRICK ST | Auckland | TPAP K17 | 2024-12-07 | 45633.4132 | 2024-12-07 | 45633.4514 | 8.786e-05 | 1.597e-06 | 1 | 55 | Planned | Planned
2614 |  | 36870 | LIVE J01 - J01 AOTEA | Auckland | LIVE J01 | 2024-12-07 | 45633.4729 | 2024-12-07 | 45633.875 | 0.013586 | 4.7924e-05 | 15 | 8505 | Unplanned | Third party interference
2615 |  | 36871 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2024-12-07 | 45633.8965 | 2024-12-08 | 45634.2125 | 0.05306 | 0.00011661 | 73 | 33215 | Planned | Planned
2616 |  | 36872 | DRIV K02 - K02 WILDING AVE | Auckland | DRIV K02 | 2024-12-07 | 45633.9583 | 2024-12-08 | 45634.2382 | 0.084335 | 0.00020927 | 131 | 52793 | Planned | Planned
2617 |  | 36874 | HVAL K02 - K02 CORBAN AVENUE | Northern | HVAL K02 | 2024-12-08 | 45634.3333 | 2024-12-08 | 45634.5174 | 0.00042333 | 1.597e-06 | 1 | 265 | Planned | Planned
2618 |  | 36875 | WAIK K01 - K01 ARIES | Northern | WAIK K01 | 2024-12-08 | 45634.3549 | 2024-12-08 | 45634.691 | 0.021649 | 4.4729e-05 | 28 | 13552 | Planned | Planned
2619 |  | 36876 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2024-12-08 | 45634.3854 | 2024-12-08 | 45634.5542 | 0.0044984 | 1.917e-05 | 12 | 2816 | Planned | Planned
2620 |  | 36877 | OTAR K15 - K15 NZ WINES & SPIRITS | Auckland | OTAR K15 | 2024-12-08 | 45634.6076 | 2024-12-08 | 45634.7486 | 0.0012971 | 6.39e-06 | 4 | 812 | Unplanned | Cause unknown
2621 |  | 36879 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-12-08 | 45634.6833 | 2024-12-08 | 45634.8444 | 0.0022237 | 9.585e-06 | 6 | 1392 | Unplanned | Vegetation
2622 |  | 36881 | DRIV K13 - K13 KING EDWARD AVE | Auckland | DRIV K13 | 2024-12-08 | 45634.9375 | 2024-12-09 | 45635.1674 | 0.075613 | 0.00022844 | 143 | 47333 | Planned | Planned
2623 |  | 36882 | LIVE K18 - K18 QUEEN CITY APARTMENTS | Auckland | LIVE K18 | 2024-12-09 | 45635.0208 | 2024-12-09 | 45635.1889 | 0.072291 | 0.00029873 | 187 | 45254 | Planned | Planned
2624 |  | 36883 | ROSE K01 - K01 GLUCINA SMELTERS | Auckland | ROSE K01 | 2024-12-09 | 45635.125 | 2024-12-09 | 45635.3458 | 0.001524 | 4.792e-06 | 3 | 954 | Planned | Planned
2625 |  | 36884 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-12-09 | 45635.3438 | 2024-12-09 | 45635.7514 | 0.010984 | 3.834e-05 | 12 | 6876 | Planned | Planned
2626 |  | 36885 | BROW K11 - K11 SARTORS AVE | Northern | BROW K11 | 2024-12-09 | 45635.3382 | 2024-12-09 | 45635.7701 | 0.068636 | 0.00011661 | 73 | 42966 | Planned | Planned
2627 |  | 36886 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-12-09 | 45635.4375 | 2024-12-09 | 45635.5417 | 0.00071886 | 4.792e-06 | 3 | 450 | Planned | Planned
2628 |  | 36887 | NSBT83 - ORATIA H01 - LAINGHOLM P290 (83) | Northern | LAIN K09 | 2024-12-09 | 45635.4403 | 2024-12-09 | 45635.6528 | 0.004754 | 4.9521e-05 | 31 | 2976 | Unplanned | Defective equipment
2629 |  | 36888 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-12-09 | 45635.4736 | 2024-12-09 | 45635.6521 | 0.061616 | 0.0017364 | 1087 | 38571 | Unplanned | Vegetation
2630 |  | 36889 | HPOI K07 - K07 POTTERY CRES | Northern | HPOI K07 | 2024-12-09 | 45635.8847 | 2024-12-10 | 45636.1424 | 0.091229 | 0.0023339 | 690 | 57109 | Unplanned | Defective equipment
2631 |  | 36890 | TORB K10 - K10 DEEP CREEK ROAD | Northern | TORB K10 | 2024-12-09 | 45635.8951 | 2024-12-10 | 45636.1243 | 0.17104 | 0.00077318 | 484 | 107070 | Unplanned | Defective equipment
2632 |  | 36890 | TORB K10 - K10 DEEP CREEK ROAD | Northern | TORB K11 | 2024-12-09 | 45635.8951 | 2024-12-10 | 45636.1243 | 0.1145 | 0.0030639 | 1918 | 71678 | Unplanned | Defective equipment
2633 |  | 36891 | MNAB K02 - K02 GAVIN ST WEST | Auckland | MNAB K02 | 2024-12-09 | 45635.9583 | 2024-12-10 | 45636.0472 | 0.0024537 | 1.917e-05 | 12 | 1536 | Planned | Planned
2634 |  | 36893 | QUAY K09 - K09 SHELL SERVICE STN | Auckland | QUAY K09 | 2024-12-09 | 45635.9681 | 2024-12-10 | 45636.0625 | 0.0060831 | 4.4729e-05 | 28 | 3808 | Planned | Planned
2635 |  | 36894 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-12-10 | 45636.0417 | 2024-12-10 | 45636.1021 | 0.028491 | 0.00032748 | 205 | 17835 | Planned | Planned
2636 |  | 36895 | MNAB K34 - K34 525 GREAT SOUTH RD | Auckland | MNAB K34 | 2024-12-10 | 45636.0847 | 2024-12-10 | 45636.1687 | 0.0028994 | 2.3962e-05 | 15 | 1815 | Planned | Planned
2637 |  | 36896 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-12-10 | 45636.2118 | 2024-12-10 | 45636.7903 | 0.017701 | 0.0011502 | 720 | 11081 | Planned | Planned
2638 |  | 36897 | NLYN K04 - K04 RATA ST | Northern | NLYN K04 | 2024-12-10 | 45636.3542 | 2024-12-10 | 45636.6764 | 0.23052 | 0.00049681 | 311 | 144304 | Planned | Planned
2639 |  | 36898 | RANU K02 - K02 ZITA MARIA | Northern | RANU K02 | 2024-12-10 | 45636.3562 | 2024-12-10 | 45636.6653 | 0.0049761 | 1.1182e-05 | 7 | 3115 | Planned | Planned
2640 |  | 36899 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2024-12-10 | 45636.3854 | 2024-12-10 | 45636.5299 | 0.025917 | 0.00012459 | 78 | 16224 | Planned | Planned
2641 |  | 36900 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-12-10 | 45636.3972 | 2024-12-10 | 45636.4181 | 0.0020128 | 6.7089e-05 | 42 | 1260 | Planned | Planned
2642 |  | 36901 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-12-10 | 45636.3611 | 2024-12-10 | 45636.7403 | 0.050516 | 9.2654e-05 | 58 | 31623 | Planned | Planned
2643 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | CLEV R134 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.0038978 | 0.00019486 | 122 | 2440 | Unplanned | Vegetation
2644 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | CLEV R140 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.033834 | 0.0016916 | 1059 | 21180 | Unplanned | Vegetation
2645 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | MARA K01 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.051232 | 0.003941 | 2467 | 32071 | Unplanned | Vegetation
2646 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | MARA K04 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.019874 | 0.0015288 | 957 | 12441 | Unplanned | Vegetation
2647 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | MARA K05 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.041721 | 0.0008275 | 518 | 26117 | Unplanned | Vegetation
2648 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | MARA K08 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.00085145 | 6.5496e-05 | 41 | 533 | Unplanned | Vegetation
2649 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | MARA K10 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.0045064 | 0.00034665 | 217 | 2821 | Unplanned | Vegetation
2650 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | MARA K11 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.0042988 | 0.00033068 | 207 | 2691 | Unplanned | Vegetation
2651 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | WAIH K02 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.022075 | 0.0016982 | 1063 | 13819 | Unplanned | Vegetation
2652 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | WAIH K03 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.04332 | 0.0033323 | 2086 | 27118 | Unplanned | Vegetation
2653 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | WAIH K05 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.040724 | 0.0031327 | 1961 | 25493 | Unplanned | Vegetation
2654 |  | 36902 | ASBT274B - CLEVEDON H03 - MARAETAI H02 | Auckland | WAIH K06 | 2024-12-10 | 45636.5118 | 2024-12-10 | 45636.5701 | 0.025336 | 0.0019489 | 1220 | 15860 | Unplanned | Vegetation
2655 |  | 36903 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-12-10 | 45636.5417 | 2024-12-10 | 45636.6056 | 0.0066135 | 7.1886e-05 | 45 | 4140 | Planned | Planned
2656 |  | 36904 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-10 | 45636.5875 | 2024-12-10 | 45636.6451 | 0.013789 | 0.00016613 | 104 | 8632 | Unplanned | Vegetation
2657 |  | 36905 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2024-12-10 | 45636.5813 | 2024-12-10 | 45636.7903 | 0.23995 | 0.0011501 | 720 | 150206 | Unplanned | Human error
2658 |  | 36906 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2024-12-10 | 45636.7222 | 2024-12-11 | 45637.6222 | 0.0044473 | 1.4376e-05 | 5 | 2784 | Unplanned | Defective equipment
2659 |  | 36907 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-12-10 | 45636.7104 | 2024-12-10 | 45636.9993 | 0.011962 | 2.8754e-05 | 18 | 7488 | Planned | Planned
2660 |  | 36908 | ROSE K16 - K16 432 ROSEBANK RD | Auckland | ROSE K16 | 2024-12-10 | 45636.9583 | 2024-12-11 | 45637.0417 | 0.0028754 | 2.3962e-05 | 15 | 1800 | Planned | Planned
2661 |  | 36909 | TRIA K09 - K09 ROYAL ROAD | Northern | TRIA K03 | 2024-12-11 | 45637.2083 | 2024-12-11 | 45637.6715 | 0.070774 | 0.00016614 | 104 | 44304 | Planned | Planned
2662 |  | 36909 | TRIA K09 - K09 ROYAL ROAD | Northern | TRIA K09 | 2024-12-11 | 45637.2083 | 2024-12-11 | 45637.6715 | 0.0063387 | 9.9043e-05 | 62 | 3968 | Planned | Planned
2663 |  | 36910 | MKIN K01 - K01 MUNROE LANE + LS | Northern | MKIN K01 | 2024-12-11 | 45637.375 | 2024-12-11 | 45637.5972 | 0.067477 | 0.00021086 | 132 | 42240 | Planned | Planned
2664 |  | 36911 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2024-12-11 | 45637.3958 | 2024-12-11 | 45637.5417 | 0.010399 | 4.952e-05 | 31 | 6510 | Planned | Planned
2665 |  | 36912 | TRIA K03 - K03 COLWILL RD | Northern | TRIA K03 | 2024-12-11 | 45637.3826 | 2024-12-11 | 45637.4097 | 0.058625 | 0.0015032 | 941 | 36699 | Unplanned | Defective equipment
2666 |  | 36913 | WIRI K15 - K15 KEITH HAY DR | Auckland | WIRI K15 | 2024-12-11 | 45637.6667 | 2024-12-11 | 45637.6833 | 0.0012268 | 5.1119e-05 | 32 | 768 | Planned | Planned
2667 |  | 36914 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2024-12-11 | 45637.784 | 2024-12-11 | 45637.8542 | 0.0011294 | 1.1182e-05 | 7 | 707 | Unplanned | Wildlife
2668 |  | 36915 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-11 | 45637.8868 | 2024-12-11 | 45637.9451 | 0.0032205 | 3.8336e-05 | 24 | 2016 | Unplanned | Defective equipment
2669 |  | 36916 | REMU K18 - K18 HAAST ST | Auckland | REMU K18 | 2024-12-12 | 45638.0833 | 2024-12-12 | 45638.175 | 0.012019 | 9.1055e-05 | 57 | 7524 | Planned | Planned
2670 |  | 36917 | REMU K18 - K18 HAAST ST | Auckland | REMU K18 | 2024-12-11 | 45637.9583 | 2024-12-12 | 45638.0528 | 0.02455 | 0.00018051 | 113 | 15368 | Planned | Planned
2671 |  | 36918 | QUAY K09 - K09 SHELL SERVICE STN | Auckland | QUAY K09 | 2024-12-11 | 45637.9583 | 2024-12-12 | 45638.075 | 0.012949 | 7.8277e-05 | 49 | 8106 | Planned | Planned
2672 |  | 36919 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-12-11 | 45637.9028 | 2024-12-12 | 45638.0312 | 0.00059106 | 3.195e-06 | 2 | 370 | Unplanned | Vegetation
2673 |  | 36920 | AVON K13 - K13 CHALMERS ST. VIA LOCAL S/S | Auckland | AVON K13 | 2024-12-12 | 45638.0417 | 2024-12-12 | 45638.0819 | 0.018994 | 0.00032748 | 205 | 11890 | Planned | Planned
2674 |  | 36921 | TRIA K09 - K09 ROYAL ROAD | Northern | TRIA K09 | 2024-12-12 | 45638.2083 | 2024-12-12 | 45638.2444 | 0.0042876 | 9.9044e-05 | 62 | 2684 | Planned | Planned
2675 |  | 36922 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-12-12 | 45638.3715 | 2024-12-12 | 45638.741 | 0.021793 | 0.00010064 | 44 | 13642 | Planned | Planned
2676 |  | 36923 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2024-12-12 | 45638.359 | 2024-12-12 | 45638.5278 | 0.00038818 | 1.597e-06 | 1 | 243 | Unplanned | Vegetation
2677 |  | 36924 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-12-12 | 45638.375 | 2024-12-12 | 45638.5903 | 0.0059425 | 1.9168e-05 | 12 | 3720 | Planned | Planned
2678 |  | 36926 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-12-12 | 45638.441 | 2024-12-12 | 45638.4861 | 0.00010383 | 1.597e-06 | 1 | 65 | Unplanned | Vegetation
2679 |  | 36927 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-12-12 | 45638.4042 | 2024-12-12 | 45638.5479 | 0.00099202 | 4.792e-06 | 3 | 621 | Unplanned | Vegetation
2680 |  | 36929 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2024-12-12 | 45638.7875 | 2024-12-13 | 45639.5306 | 0.068371 | 6.3898e-05 | 40 | 42800 | Unplanned | Vegetation
2681 |  | 36930 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-12-12 | 45638.8292 | 2024-12-12 | 45638.8604 | 0.00071886 | 1.5974e-05 | 10 | 450 | Unplanned | Cause unknown
2682 |  | 36932 | NLYN K05 - K05 KELSTON | Northern | NLYN K05 | 2024-12-12 | 45638.941 | 2024-12-13 | 45639.1319 | 0.016447 | 6.2302e-05 | 39 | 10296 | Planned | Planned
2683 |  | 36932 | NLYN K05 - K05 KELSTON | Northern | SABU K08 | 2024-12-12 | 45638.941 | 2024-12-13 | 45639.1319 | 0.017356 | 6.5498e-05 | 41 | 10865 | Planned | Planned
2684 |  | 36933 | TAKA K11 - K11 HAMLINS AND CAP BANK | Auckland | TAKA K11 | 2024-12-12 | 45638.9507 | 2024-12-13 | 45639.1069 | 0.024801 | 0.00011022 | 69 | 15525 | Unplanned | Third party interference
2685 |  | 36934 | AVON K02 - K02 ST JUDE ST.(PENSIONER FLATS) | Auckland | AVON K02 | 2024-12-12 | 45638.9583 | 2024-12-13 | 45639.0424 | 0.01353 | 0.00011182 | 70 | 8470 | Planned | Planned
2686 |  | 36935 | HILL K02 - K02 72 HILLSBOROUGH RD | Auckland | HILL K02 | 2024-12-13 | 45639.0833 | 2024-12-13 | 45639.1694 | 0.027534 | 0.00022205 | 139 | 17236 | Planned | Planned
2687 |  | 36937 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-12-13 | 45639.2583 | 2024-12-13 | 45639.3729 | 0.0018451 | 1.1182e-05 | 7 | 1155 | Unplanned | Vegetation
2688 |  | 36938 | BIRK K11 - K11 BEACH HAVEN | Northern | BIRK K11 | 2024-12-13 | 45639.3479 | 2024-12-13 | 45639.3701 | 0.037112 | 0.0011598 | 726 | 23232 | Unplanned | Wildlife
2689 |  | 36939 | WOOD K02 - K02 SEL PEACOCK DR | Northern | WOOD K02 | 2024-12-13 | 45639.375 | 2024-12-13 | 45639.6174 | 0.001115 | 3.195e-06 | 2 | 698 | Planned | Planned
2690 |  | 36940 | MANL K10 - K10 MATAI ROAD | Northern | MANL K10 | 2024-12-13 | 45639.4104 | 2024-12-13 | 45639.4451 | 0.038171 | 0.0016118 | 1009 | 23895 | Unplanned | Wildlife
2691 |  | 36941 | SAND K18 - K18 SANDRINGHAM RD EXTN - SOUTH | Auckland | SAND K18 | 2024-12-13 | 45639.4201 | 2024-12-13 | 45639.6965 | 0.086186 | 0.00022524 | 141 | 53952 | Planned | Planned
2692 |  | 36942 | MWEL K03 - K03 BRISCOES | Auckland | MWEL K03 | 2024-12-13 | 45639.4646 | 2024-12-13 | 45639.6097 | 0.00033387 | 1.597e-06 | 1 | 209 | Unplanned | Defective equipment
2693 |  | 36943 | BROW K11 - K11 SARTORS AVE | Northern | BROW K11 | 2024-12-13 | 45639.6694 | 2024-12-13 | 45639.6931 | 0.0021725 | 6.3898e-05 | 40 | 1360 | Planned | Planned
2694 |  | 36944 | QUAY K09 - K09 SHELL SERVICE STN | Auckland | QUAY K09 | 2024-12-14 | 45640.0424 | 2024-12-14 | 45640.134 | 0.0044282 | 3.3547e-05 | 21 | 2772 | Planned | Planned
2695 |  | 36945 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-14 | 45640.3007 | 2024-12-14 | 45640.3715 | 0.0008147 | 7.987e-06 | 5 | 510 | Unplanned | Cause unknown
2696 |  | 36948 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-12-14 | 45640.5924 | 2024-12-14 | 45640.6562 | 0.0004409 | 4.792e-06 | 3 | 276 | Unplanned | Vegetation
2697 |  | 36949 | NEWT K09 - K09 A.R.A. WATERWORKS | Auckland | NEWT K09 | 2024-12-15 | 45641.2875 | 2024-12-15 | 45641.4528 | 0.0026614 | 1.1182e-05 | 7 | 1666 | Unplanned | Defective equipment
2698 |  | 36950 | TPAP K08 - K08 CHURCH ST WEST VIA LS | Auckland | TPAP K08 | 2024-12-15 | 45641.5639 | 2024-12-16 | 45642.4694 | 0.012499 | 9.585e-06 | 6 | 7824 | Unplanned | Defective equipment
2699 |  | 36951 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2024-12-15 | 45641.6097 | 2024-12-15 | 45641.8333 | 0.037035 | 0.00011502 | 72 | 23184 | Unplanned | Defective equipment
2700 |  | 36952 | ORAT K06 - K06 GLENGARRY ROAD | Northern | ORAT K06 | 2024-12-15 | 45641.6951 | 2024-12-15 | 45641.8264 | 0.010567 | 5.5911e-05 | 35 | 6615 | Unplanned | Defective equipment
2701 |  | 36953 | MKAU K09 - K09 CAVENDISH CENTRE | Auckland | MKAU K09 | 2024-12-15 | 45641.6639 | 2024-12-15 | 45641.8125 | 0.0066566 | 7.9873e-05 | 50 | 4167 | Unplanned | Cause unknown
2702 |  | 36954 | MKAU K12 - K12 LAMBIE DRIVE | Auckland | MKAU K12 | 2024-12-15 | 45641.7646 | 2024-12-16 | 45642.2507 | 0.33031 | 0.0018499 | 955 | 206775 | Unplanned | Third party interference
2703 |  | 36955 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2024-12-15 | 45641.7424 | 2024-12-15 | 45641.7826 | 0.0040767 | 7.0288e-05 | 44 | 2552 | Unplanned | Cause unknown
2704 |  | 36956 | MKAU K07 - K07 TE IRIRANGI DRIVE | Auckland | MKAU K07 | 2024-12-15 | 45641.8583 | 2024-12-15 | 45641.9701 | 0.20365 | 0.0048179 | 2225 | 127485 | Unplanned | Cause unknown
2705 |  | 36957 | ROSE K15 - K15 BEATRIX ROAD VIA LOCAL | Auckland | ROSE K15 | 2024-12-16 | 45642.2104 | 2024-12-16 | 45642.2812 | 0.13609 | 0.0013499 | 845 | 85189 | Planned | Planned
2706 |  | 36958 | GINN K02 - K02 PADDINGTON ST | Auckland | GINN K02 | 2024-12-16 | 45642.0896 | 2024-12-16 | 45642.1465 | 0.025016 | 0.00083387 | 261 | 15660 | Unplanned | Cause unknown
2707 |  | 36958 | GINN K02 - K02 PADDINGTON ST | Auckland | SHEL K06 | 2024-12-16 | 45642.0896 | 2024-12-16 | 45642.1465 | 0.054886 | 0.00066933 | 419 | 34358 | Unplanned | Cause unknown
2708 |  | 36959 | NLYN K01 - K01 ARAWA ST | Northern | NLYN K01 | 2024-12-16 | 45642.2493 | 2024-12-16 | 45642.7361 | 0.085106 | 0.00012141 | 76 | 53276 | Unplanned | Defective equipment
2709 |  | 36960 | GREE K09 - K09 SPRINGS RD No.2 | Auckland | GREE K09 | 2024-12-16 | 45642.2861 | 2024-12-17 | 45643.4292 | 0.00049202 | 6.391e-06 | 2 | 308 | Unplanned | Cause unknown
2710 |  | 36961 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-12-16 | 45642.3938 | 2024-12-17 | 45643.6111 | 0.047435 | 0.00035305 | 167 | 29694 | Unplanned | Defective equipment
2711 |  | 36963 | MANL K10 - K10 MATAI ROAD | Northern | MANL K10 | 2024-12-16 | 45642.5361 | 2024-12-16 | 45642.5889 | 0.006556 | 8.6263e-05 | 54 | 4104 | Unplanned | Defective equipment
2712 |  | 36964 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2024-12-16 | 45642.575 | 2024-12-16 | 45642.6646 | 0.040596 | 0.0003147 | 197 | 25413 | Unplanned | Vegetation
2713 |  | 36965 | KING K01 - K01 DOMINION RD | Auckland | BALM K04 | 2024-12-16 | 45642.5826 | 2024-12-16 | 45642.8757 | 0.034045 | 0.0009457 | 592 | 21312 | Unplanned | Lightning
2714 |  | 36965 | KING K01 - K01 DOMINION RD | Auckland | KING K01 | 2024-12-16 | 45642.5826 | 2024-12-16 | 45642.8757 | 0.11707 | 0.0011294 | 623 | 73286 | Unplanned | Lightning
2715 |  | 36966 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2024-12-16 | 45642.3736 | 2024-12-16 | 45642.6451 | 0.003123 | 7.987e-06 | 5 | 1955 | Unplanned | Cause unknown
2716 |  | 36968 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-12-16 | 45642.7486 | 2024-12-16 | 45642.8889 | 0.030491 | 0.0014888 | 932 | 19087 | Unplanned | Defective equipment
2717 |  | 36969 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2024-12-16 | 45642.75 | 2024-12-17 | 45643.8333 | 0.0057125 | 4.4732e-05 | 14 | 3576 | Planned | Planned
2718 |  | 36970 | SHOW K02 - K02 GILLET PL | Auckland | SHOW K02 | 2024-12-16 | 45642.9583 | 2024-12-17 | 45643.0375 | 0.011655 | 0.00010224 | 64 | 7296 | Planned | Planned
2719 |  | 36971 | ORAT K06 - K06 GLENGARRY ROAD | Northern | ORAT K06 | 2024-12-16 | 45642.9542 | 2024-12-16 | 45642.9722 | 0.0014537 | 5.5911e-05 | 35 | 910 | Unplanned | Defective equipment
2720 |  | 36972 | PARN K07 - K07 AUCKLAND GLASS VIA LS | Auckland | PARN K07 | 2024-12-17 | 45643.0069 | 2024-12-17 | 45643.0104 | 0.00072684 | 0.00014537 | 91 | 455 | Unplanned | Other Cause | Outage caused by Tap Operation
2721 |  | 36973 | CHEV K11 - K11 ANDY MILLER LTD VIA LS | Auckland | CHEV K11 | 2024-12-17 | 45643.0417 | 2024-12-18 | 45644.0958 | 0.097317 | 0.00078116 | 199 | 60920 | Planned | Planned
2722 |  | 36974 | GREE K08 - K08 GREENMOUNT DRIVE VIA LS | Auckland | GREE K08 | 2024-12-17 | 45643.0833 | 2024-12-17 | 45643.1639 | 0.0014824 | 1.278e-05 | 8 | 928 | Planned | Planned
2723 |  | 36975 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2024-12-17 | 45643.4347 | 2024-12-17 | 45643.5569 | 0.009278 | 5.2713e-05 | 33 | 5808 | Planned | Planned
2724 |  | 36976 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-12-17 | 45643.3431 | 2024-12-17 | 45643.6875 | 0.063387 | 0.0001278 | 80 | 39680 | Planned | Planned
2725 |  | 36977 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-12-17 | 45643.375 | 2024-12-17 | 45643.6035 | 0.0036789 | 1.1182e-05 | 7 | 2303 | Planned | Planned
2726 |  | 36978 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-17 | 45643.3861 | 2024-12-17 | 45643.5979 | 0.050671 | 0.00016613 | 104 | 31720 | Planned | Planned
2727 |  | 36979 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-12-17 | 45643.434 | 2024-12-17 | 45643.6403 | 0.0037956 | 1.2779e-05 | 8 | 2376 | Planned | Planned
2728 |  | 36980 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-12-17 | 45643.4181 | 2024-12-17 | 45643.7292 | 0.004294 | 9.584e-06 | 6 | 2688 | Unplanned | Defective equipment
2729 |  | 36982 | CLEN K07 - K07 ROBERT ROSS | Auckland | CLEN K07 | 2024-12-17 | 45643.3264 | 2024-12-17 | 45643.3278 | 0.001492 | 0.00074601 | 467 | 934 | Unplanned | Human error
2730 |  | 36983 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2024-12-17 | 45643.2799 | 2024-12-17 | 45643.3264 | 0.0099538 | 0.00014856 | 93 | 6231 | Unplanned | Wildlife
2731 |  | 36985 | NEWM K15 - K15 EDEN ST CARPENTERS | Auckland | NEWM K15 | 2024-12-17 | 45643.925 | 2024-12-18 | 45644.1472 | 0.0010224 | 3.195e-06 | 2 | 640 | Planned | Planned
2732 |  | 36986 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2024-12-17 | 45643.9583 | 2024-12-18 | 45644.0396 | 0.009532 | 8.147e-05 | 51 | 5967 | Planned | Planned
2733 |  | 36987 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2024-12-18 | 45644.041 | 2024-12-18 | 45644.0924 | 0.017732 | 0.00023962 | 150 | 11100 | Unplanned | Vegetation
2734 |  | 36990 | ROCK K15 - K15 MAROA RD | Auckland | ROCK K15 | 2024-12-18 | 45644.1424 | 2024-12-18 | 45644.1493 | 0.0027157 | 0.00027157 | 170 | 1700 | Unplanned | Other Cause | Outage caused by Tap Operation
2735 |  | 36991 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-12-18 | 45644.3403 | 2024-12-18 | 45644.6229 | 0.0097525 | 2.3962e-05 | 15 | 6105 | Planned | Planned
2736 |  | 36992 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-12-18 | 45644.3333 | 2024-12-18 | 45644.6424 | 0.0063978 | 1.4376e-05 | 9 | 4005 | Planned | Planned
2737 |  | 36993 | MANL K04 - K04 RISHWORTH | Northern | MANL K04 | 2024-12-18 | 45644.375 | 2024-12-18 | 45644.5979 | 0.02769 | 8.6263e-05 | 54 | 17334 | Planned | Planned
2738 |  | 36994 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-18 | 45644.375 | 2024-12-18 | 45644.7118 | 0.0054234 | 1.1182e-05 | 7 | 3395 | Planned | Planned
2739 |  | 36996 | MEAS K20 - K20 ALLEN ST | Auckland | MEAS K20 | 2024-12-18 | 45644.684 | 2024-12-18 | 45644.8056 | 0.02544 | 0.00014537 | 91 | 15925 | Unplanned | Cause unknown
2740 |  | 36997 | NEWM K30 - K30 BP CROWHURST ST | Auckland | NEWM K30 | 2024-12-18 | 45644.9792 | 2024-12-19 | 45645.1521 | 0.038186 | 0.00015336 | 96 | 23904 | Planned | Planned
2741 |  | 36998 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2024-12-19 | 45645.1347 | 2024-12-19 | 45645.1771 | 0.038881 | 0.00063739 | 399 | 24339 | Unplanned | Defective equipment
2742 |  | 36999 | ROSE K15 - K15 BEATRIX ROAD VIA LOCAL | Auckland | ROSE K15 | 2024-12-19 | 45645.2174 | 2024-12-19 | 45645.2785 | 0.10391 | 0.0013467 | 843 | 65049 | Planned | Planned
2743 |  | 37000 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2024-12-19 | 45645.2951 | 2024-12-19 | 45645.6049 | 0.045061 | 0.00013099 | 82 | 28208 | Planned | Planned
2744 |  | 37001 | ECOA K04 - K04 KNIGHTS ROAD | Northern | ECOA K04 | 2024-12-19 | 45645.3646 | 2024-12-19 | 45645.6771 | 0.071167 | 0.00015815 | 99 | 44550 | Planned | Planned
2745 |  | 37002 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-12-19 | 45645.434 | 2024-12-19 | 45645.5111 | 0.031884 | 0.00074121 | 464 | 19959 | Unplanned | Third party interference
2746 |  | 37003 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-19 | 45645.4028 | 2024-12-19 | 45645.7326 | 0.0053116 | 1.1181e-05 | 7 | 3325 | Unplanned | Third party interference
2747 |  | 37004 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-12-19 | 45645.4688 | 2024-12-19 | 45645.5 | 0.0005032 | 1.1182e-05 | 7 | 315 | Unplanned | Other Cause | Outage caused by Tap Operation
2748 |  | 37005 | TPAP K08 - K08 CHURCH ST WEST VIA LS | Auckland | TPAP K08 | 2024-12-19 | 45645.4097 | 2024-12-19 | 45645.4736 | 0.0008818 | 9.585e-06 | 6 | 552 | Unplanned | Defective equipment
2749 |  | 37007 | MEAS K20 - K20 ALLEN ST | Auckland | MEAS K20 | 2024-12-19 | 45645.1972 | 2024-12-19 | 45645.6389 | 0.093309 | 0.00029713 | 186 | 58411 | Unplanned | Cause unknown
2750 |  | 37008 | SJOH K02 - K02 175 LINE RD | Auckland | SJOH K02 | 2024-12-19 | 45645.9792 | 2024-12-20 | 45646.1479 | 0.099763 | 0.00041055 | 257 | 62451 | Planned | Planned
2751 |  | 37009 | ROSE K08 - K08 HONAN PL PHIPPS ROCOL | Auckland | ROSE K08 | 2024-12-19 | 45645.9896 | 2024-12-20 | 45646.0597 | 0.047435 | 0.00046965 | 294 | 29694 | Planned | Planned
2752 |  | 37011 | GREE K09 - K09 SPRINGS RD No.2 | Auckland | GREE K09 | 2024-12-20 | 45646.4389 | 2024-12-20 | 45646.4465 | 1.7572e-05 | 1.597e-06 | 1 | 11 | Unplanned | Defective equipment
2753 |  | 37015 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2024-12-21 | 45647.5556 | 2024-12-21 | 45647.5785 | 0.0020032 | 6.0703e-05 | 38 | 1254 | Unplanned | Vegetation
2754 |  | 37016 | BIRK K05 - K05 FORDHAM STREET | Northern | BIRK K05 | 2024-12-21 | 45647.6125 | 2024-12-21 | 45647.6639 | 0.1045 | 0.0014122 | 884 | 65416 | Unplanned | Cause unknown
2755 |  | 37017 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-12-21 | 45647.591 | 2024-12-21 | 45647.6007 | 0.00024601 | 1.7572e-05 | 11 | 154 | Unplanned | Other Cause | Outage caused by Tap Operation
2756 |  | 37020 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-21 | 45647.7528 | 2024-12-21 | 45647.7812 | 0.0023578 | 5.7509e-05 | 36 | 1476 | Unplanned | Defective equipment
2757 |  | 37021 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2024-12-21 | 45647.9153 | 2024-12-22 | 45648.9576 | 0.10798 | 0.00052235 | 122 | 67593 | Unplanned | Defective equipment
2758 |  | 37022 | MANU K03 - K03 COXHEAD RD | Auckland | MANU K03 | 2024-12-23 | 45649.3028 | 2024-12-23 | 45649.3854 | 0.026444 | 0.00024441 | 153 | 16554 | Unplanned | Wildlife
2759 |  | 37023 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2024-12-23 | 45649.4389 | 2024-12-23 | 45649.4444 | 0.0012907 | 0.00016134 | 101 | 808 | Unplanned | Defective equipment
2760 |  | 37024 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-12-23 | 45649.5521 | 2024-12-23 | 45649.5563 | 4.7924e-05 | 7.987e-06 | 5 | 30 | Unplanned | Other Cause | Outage caused by Tap Operation
2761 |  | 37025 | HOWI K01 - K01 CASTLETON DR VIA LS | Auckland | HOWI K01 | 2024-12-24 | 45650.2403 | 2024-12-24 | 45650.3771 | 0.022526 | 0.00029553 | 185 | 14101 | Unplanned | Cause unknown
2762 |  | 37026 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-12-24 | 45650.6042 | 2024-12-24 | 45650.65 | 0.0094554 | 0.00097448 | 483 | 5919 | Unplanned | Vegetation
2763 |  | 37028 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-12-24 | 45650.9451 | 2024-12-25 | 45651.0201 | 0.011713 | 0.00015816 | 99 | 7332 | Unplanned | Vegetation
2764 |  | 37030 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-12-25 | 45651.8514 | 2024-12-26 | 45652.5819 | 0.010083 | 9.585e-06 | 6 | 6312 | Unplanned | Vegetation
2765 |  | 37031 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-12-26 | 45652.0965 | 2024-12-26 | 45652.1715 | 0.0157 | 0.00014536 | 91 | 9828 | Unplanned | Wildlife
2766 |  | 37032 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2024-12-26 | 45652.25 | 2024-12-26 | 45652.3153 | 0.054269 | 0.0006294 | 394 | 33972 | Unplanned | Vegetation
2767 |  | 37034 | OREW K10 - K10 HATFIELDS | Northern | OREW K10 | 2024-12-26 | 45652.2847 | 2024-12-26 | 45652.3562 | 0.10914 | 0.003008 | 1883 | 68318 | Unplanned | Wildlife
2768 |  | 37036 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-12-27 | 45653.3382 | 2024-12-27 | 45653.4208 | 0.0032317 | 2.7157e-05 | 17 | 2023 | Unplanned | Vegetation
2769 |  | 37039 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2024-12-27 | 45653.5062 | 2024-12-27 | 45653.5715 | 0.010949 | 0.00037221 | 233 | 6854 | Unplanned | Cause unknown
2770 |  | 37040 | KKAP K04 - K04 GLORIT | Northern | KKAP K02 | 2024-12-27 | 45653.5111 | 2024-12-28 | 45654.5563 | 0.060691 | 0.0011311 | 708 | 37992 | Unplanned | Vegetation
2771 |  | 37040 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-12-27 | 45653.5111 | 2024-12-28 | 45654.5563 | 0.38391 | 0.0014298 | 397 | 240327 | Unplanned | Vegetation
2772 |  | 37041 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2024-12-27 | 45653.5222 | 2024-12-27 | 45653.5785 | 0.049989 | 0.00085146 | 533 | 31293 | Unplanned | Cause unknown
2773 |  | 37042 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2024-12-27 | 45653.5236 | 2024-12-28 | 45654.0681 | 0.25706 | 0.0011869 | 743 | 160920 | Unplanned | Defective equipment
2774 |  | 37043 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2024-12-27 | 45653.5312 | 2024-12-27 | 45653.6146 | 0.13891 | 0.0018946 | 1186 | 86956 | Unplanned | Vegetation
2775 |  | 37045 | GHIT K08 - K08 BERNARD MAGNUS LN | Northern | GHIT K08 | 2024-12-27 | 45653.5361 | 2024-12-27 | 45653.5931 | 0.046371 | 0.0005655 | 354 | 29028 | Unplanned | Cause unknown
2776 |  | 37046 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-27 | 45653.5368 | 2024-12-27 | 45653.8993 | 0.10993 | 0.00050001 | 313 | 68817 | Unplanned | Defective equipment
2777 |  | 37047 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-27 | 45653.541 | 2024-12-27 | 45653.9028 | 0.29431 | 0.00064061 | 401 | 184239 | Unplanned | Defective equipment
2778 |  | 37048 | KEEL K12 - K12 STURGES RD | Northern | KEEL K12 | 2024-12-27 | 45653.5375 | 2024-12-27 | 45653.6896 | 0.15159 | 0.0017987 | 1126 | 94894 | Unplanned | Vegetation
2779 |  | 37049 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2024-12-27 | 45653.5535 | 2024-12-27 | 45653.6931 | 0.032448 | 0.0014825 | 464 | 20312 | Unplanned | Vegetation
2780 |  | 37050 | MKIN K11 - K11 THE AVENUE | Northern | MKIN K11 | 2024-12-27 | 45653.5493 | 2024-12-27 | 45653.7632 | 0.21232 | 0.0026454 | 1468 | 132912 | Unplanned | Vegetation
2781 |  | 37051 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-27 | 45653.5722 | 2024-12-28 | 45654.1861 | 0.24454 | 0.00069806 | 437 | 153079 | Unplanned | Defective equipment
2782 |  | 37052 | RBEA K11 - K11 TITAN PL | Northern | RBEA K11 | 2024-12-27 | 45653.5736 | 2024-12-27 | 45653.6361 | 0.077769 | 0.00087381 | 547 | 48683 | Unplanned | Defective equipment
2783 |  | 37052 | RBEA K11 - K11 TITAN PL | Northern | SPUR K09 | 2024-12-27 | 45653.5736 | 2024-12-27 | 45653.6361 | 0.050751 | 0.00056392 | 353 | 31770 | Unplanned | Defective equipment
2784 |  | 37054 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-12-27 | 45653.5736 | 2024-12-27 | 45653.766 | 0.19582 | 0.00077637 | 486 | 122582 | Unplanned | Cause unknown
2785 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K02 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 3.195e-06 | 1.597e-06 | 1 | 2 | Unplanned | Cause unknown
2786 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K03 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 0.0023099 | 0.001155 | 723 | 1446 | Unplanned | Cause unknown
2787 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K04 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 0.0038978 | 0.0019489 | 1220 | 2440 | Unplanned | Cause unknown
2788 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K08 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 3.195e-06 | 1.597e-06 | 1 | 2 | Unplanned | Cause unknown
2789 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K09 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 0.0044282 | 0.0022141 | 1386 | 2772 | Unplanned | Cause unknown
2790 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K10 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 0.0024952 | 0.0012476 | 781 | 1562 | Unplanned | Cause unknown
2791 |  | 37055 | NSBT107 - WESTGATE H02 - RIVERHEAD H07 (107) | Northern | RIVE K11 | 2024-12-27 | 45653.5715 | 2024-12-28 | 45654.8507 | 0.00016933 | 8.4664e-05 | 53 | 106 | Unplanned | Cause unknown
2792 |  | 37056 | TRIA K12 - K12 UNIVERSAL DRIVE | Northern | TRIA K12 | 2024-12-27 | 45653.575 | 2024-12-27 | 45653.6438 | 0.13 | 0.0013131 | 822 | 81378 | Unplanned | Cause unknown
2793 |  | 37057 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2024-12-27 | 45653.616 | 2024-12-28 | 45654.0576 | 0.086847 | 0.00021886 | 137 | 54366 | Unplanned | Cause unknown
2794 |  | 37079 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-12-27 | 45653.4542 | 2024-12-27 | 45653.566 | 0.00077157 | 4.792e-06 | 3 | 483 | Unplanned | Cause unknown
2795 |  | 37086 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-12-27 | 45653.5194 | 2024-12-27 | 45653.6451 | 0.0034697 | 1.917e-05 | 12 | 2172 | Unplanned | Vegetation
2796 |  | 37087 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-12-27 | 45653.5215 | 2024-12-27 | 45653.5903 | 0.00094889 | 9.583e-06 | 6 | 594 | Unplanned | Vegetation
2797 |  | 37088 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-12-27 | 45653.625 | 2024-12-28 | 45654.6875 | 0.0024441 | 1.597e-06 | 1 | 1530 | Unplanned | Defective equipment
2798 |  | 37089 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-12-27 | 45653.55 | 2024-12-27 | 45653.8035 | 0.032652 | 8.9457e-05 | 56 | 20440 | Unplanned | Vegetation
2799 |  | 37090 | WSWA K03 - K03 MARSHALL LAING ST | Auckland | WSWA K03 | 2024-12-27 | 45653.6743 | 2024-12-27 | 45653.8889 | 0.05331 | 0.00017253 | 108 | 33372 | Unplanned | Cause unknown
2800 |  | 37091 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2024-12-27 | 45653.6569 | 2024-12-27 | 45653.8472 | 0.010943 | 3.9935e-05 | 25 | 6850 | Unplanned | Defective equipment
2801 |  | 37092 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-12-27 | 45653.5472 | 2024-12-27 | 45653.8542 | 0.079081 | 0.00017892 | 112 | 49504 | Unplanned | Defective equipment
2802 |  | 37093 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2024-12-27 | 45653.6375 | 2024-12-27 | 45653.8333 | 0.0054058 | 1.917e-05 | 12 | 3384 | Unplanned | Defective equipment
2803 |  | 37094 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2024-12-27 | 45653.659 | 2024-12-27 | 45653.9236 | 0.012173 | 3.1948e-05 | 20 | 7620 | Unplanned | Cause unknown
2804 |  | 37095 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-27 | 45653.559 | 2024-12-27 | 45653.8944 | 0.0038579 | 7.987e-06 | 5 | 2415 | Unplanned | Vegetation
2805 |  | 37097 | RIVE K04 - K04 BARRETT RD | Northern | RIVE K04 | 2024-12-28 | 45654.0625 | 2024-12-28 | 45654.5986 | 0.012332 | 1.5974e-05 | 10 | 7720 | Unplanned | Defective equipment
2806 |  | 37098 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2024-12-27 | 45653.5486 | 2024-12-28 | 45654.2771 | 0.033515 | 3.1947e-05 | 20 | 20980 | Unplanned | Cause unknown
2807 |  | 37099 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2024-12-27 | 45653.5507 | 2024-12-28 | 45654.3035 | 0.069266 | 6.3898e-05 | 40 | 43360 | Unplanned | Cause unknown
2808 |  | 37100 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-12-27 | 45653.559 | 2024-12-28 | 45654.3715 | 0.031773 | 2.7157e-05 | 17 | 19890 | Unplanned | Cause unknown
2809 |  | 37101 | ORAT K05 - K05 HOLDENS ROAD + LS | Northern | ORAT K05 | 2024-12-27 | 45653.5306 | 2024-12-28 | 45654.3646 | 0.0057556 | 4.792e-06 | 3 | 3603 | Unplanned | Cause unknown
2810 |  | 37102 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2024-12-27 | 45653.559 | 2024-12-28 | 45654.4458 | 0.053039 | 4.1534e-05 | 26 | 33202 | Unplanned | Cause unknown
2811 |  | 37103 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-28 | 45654.2146 | 2024-12-28 | 45654.7111 | 0.051398 | 7.188e-05 | 45 | 32175 | Unplanned | Defective equipment
2812 |  | 37104 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-12-27 | 45653.5 | 2024-12-28 | 45654.4806 | 0.027067 | 1.9169e-05 | 12 | 16944 | Unplanned | Defective equipment
2813 |  | 37105 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2024-12-28 | 45654.4472 | 2024-12-28 | 45654.5069 | 0.00013738 | 1.597e-06 | 1 | 86 | Unplanned | Defective equipment
2814 |  | 37106 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2024-12-27 | 45653.575 | 2024-12-28 | 45654.5694 | 0.011438 | 7.987e-06 | 5 | 7160 | Unplanned | Vegetation
2815 |  | 37107 | WAIM K02 - K02 ARARIMU | Northern | WAIM K02 | 2024-12-28 | 45654.5458 | 2024-12-28 | 45654.7132 | 0.06248 | 0.00094085 | 235 | 39112 | Unplanned | Vegetation
2816 |  | 37108 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-12-28 | 45654.5639 | 2024-12-28 | 45654.8465 | 0.092036 | 0.0014856 | 930 | 57614 | Unplanned | Defective equipment
2817 |  | 37109 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-12-28 | 45654.2986 | 2024-12-28 | 45654.5708 | 0.003131 | 7.987e-06 | 5 | 1960 | Unplanned | Vegetation
2818 |  | 37110 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2024-12-28 | 45654.5625 | 2024-12-28 | 45654.7188 | 0.0079074 | 3.5142e-05 | 22 | 4950 | Unplanned | Vegetation
2819 |  | 37111 | HELE K04 - K04 WAITOKI | Northern | HELE K04 | 2024-12-27 | 45653.525 | 2024-12-28 | 45654.7292 | 0.01939 | 1.1182e-05 | 7 | 12138 | Unplanned | Vegetation
2820 |  | 37112 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-28 | 45654.5965 | 2024-12-28 | 45654.9236 | 0.010548 | 4.6326e-05 | 29 | 6603 | Unplanned | Vegetation
2821 |  | 37113 | MANL K05 - K05 ARKLES BAY | Northern | MANL K05 | 2024-12-28 | 45654.8736 | 2024-12-28 | 45654.9917 | 0.06409 | 0.000377 | 236 | 40120 | Unplanned | Defective equipment
2822 |  | 37114 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-12-27 | 45653.6986 | 2024-12-28 | 45654.7986 | 0.020243 | 1.278e-05 | 8 | 12672 | Unplanned | Cause unknown
2823 |  | 37115 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2024-12-29 | 45655.0049 | 2024-12-29 | 45655.1937 | 0.037035 | 0.00057348 | 264 | 23184 | Unplanned | Vegetation
2824 |  | 37116 | TATA K10 - K10 FLANSHAW RD | Northern | TATA K10 | 2024-12-29 | 45655.1562 | 2024-12-29 | 45655.2014 | 0.039146 | 0.00060224 | 377 | 24505 | Unplanned | Defective equipment
2825 |  | 37119 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2024-12-29 | 45655.0938 | 2024-12-29 | 45655.3222 | 0.0031534 | 9.585e-06 | 6 | 1974 | Unplanned | Cause unknown
2826 |  | 37122 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2024-12-30 | 45656.5938 | 2024-12-30 | 45656.6569 | 0.10988 | 0.0033004 | 2066 | 68786 | Unplanned | Cause unknown
2827 |  | 37123 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-30 | 45656.6896 | 2024-12-30 | 45656.691 | 0.00012141 | 6.0701e-05 | 38 | 76 | Unplanned | Defective equipment
2828 |  | 37124 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2024-12-30 | 45656.7653 | 2024-12-30 | 45656.8965 | 0.032093 | 0.00018211 | 114 | 20090 | Unplanned | Vegetation
2829 |  | 37125 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2024-12-30 | 45656.7708 | 2024-12-30 | 45656.8 | 0.00033547 | 7.987e-06 | 5 | 210 | Unplanned | Defective equipment
2830 |  | 37126 | MKAU K07 - K07 TE IRIRANGI DRIVE | Auckland | MKAU K07 | 2024-12-30 | 45656.6271 | 2025-01-15 | 45672.3347 | 0.050957 | 0.00029233 | 89 | 31899 | Unplanned | Defective equipment
2831 |  | 37128 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2024-12-31 | 45657.5667 | 2024-12-31 | 45657.6125 | 0.016233 | 0.00077157 | 483 | 10162 | Unplanned | Vegetation
2832 |  | 37130 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2024-12-31 | 45657.6729 | 2025-01-01 | 45658.1875 | 0.047139 | 0.00035304 | 84 | 29509 | Unplanned | Defective equipment
2833 |  | 37133 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2024-12-31 | 45657.725 | 2024-12-31 | 45657.7806 | 0.014313 | 0.00017892 | 112 | 8960 | Unplanned | Defective equipment
2834 |  | 37136 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2024-12-31 | 45657.8264 | 2024-12-31 | 45657.8715 | 0.0021805 | 3.3546e-05 | 21 | 1365 | Unplanned | Defective equipment
2835 |  | 37137 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2024-12-31 | 45657.7931 | 2024-12-31 | 45657.9236 | 0.0012013 | 6.39e-06 | 4 | 752 | Unplanned | Vegetation
2836 |  | 37138 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2024-12-31 | 45657.7993 | 2024-12-31 | 45657.966 | 0.001917 | 7.987e-06 | 5 | 1200 | Unplanned | Vegetation
2837 |  | 37139 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2025-01-01 | 45658.4125 | 2025-01-01 | 45658.5306 | 0.097765 | 0.00057508 | 360 | 61200 | Unplanned | Third party interference
2838 |  | 37140 | CLEV R134 - CLEVEDON 3150 R134 | Auckland | CLEV R134 | 2025-01-01 | 45658.3611 | 2025-01-01 | 45658.3896 | 0.00013099 | 3.195e-06 | 2 | 82 | Unplanned | Vegetation
2839 |  | 37142 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-01-01 | 45658.7757 | 2025-01-02 | 45659.0903 | 0.00072365 | 1.597e-06 | 1 | 453 | Unplanned | Defective equipment
2840 |  | 37143 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-01-01 | 45658.9764 | 2025-01-02 | 45659.0458 | 0.0057509 | 0.00014378 | 45 | 3600 | Unplanned | Vegetation
2841 |  | 37145 | DRIV K13 - K13 KING EDWARD AVE | Auckland | DRIV K13 | 2025-01-02 | 45659.3632 | 2025-01-02 | 45659.5556 | 0.13713 | 0.0016981 | 933 | 85844 | Unplanned | Vegetation
2842 |  | 37146 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-01-02 | 45659.534 | 2025-01-02 | 45659.6132 | 0.00054633 | 4.792e-06 | 3 | 342 | Unplanned | Vegetation
2843 |  | 37147 | OTAR K15 - K15 NZ WINES & SPIRITS | Auckland | OTAR K15 | 2025-01-02 | 45659.7083 | 2025-01-03 | 45660.9653 | 0.0072652 | 1.278e-05 | 4 | 4548 | Unplanned | Defective equipment
2844 |  | 37148 | MWES K02 - K02 ORUARANGI RD | Auckland | MWES K02 | 2025-01-02 | 45659.7299 | 2025-01-03 | 45660.9882 | 0.01761 | 0.00021406 | 130 | 11024 | Unplanned | Third party interference
2845 |  | 37152 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-01-04 | 45661.1819 | 2025-01-04 | 45661.275 | 0.16014 | 0.0033003 | 2066 | 100245 | Unplanned | Cause unknown
2846 |  | 37153 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-01-04 | 45661.1819 | 2025-01-04 | 45661.2472 | 0.029732 | 0.0003163 | 198 | 18612 | Unplanned | Vegetation
2847 |  | 37155 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-01-04 | 45661.2639 | 2025-01-04 | 45661.3604 | 0.037304 | 0.00026837 | 168 | 23352 | Unplanned | Vegetation
2848 |  | 37156 | MWES K10 - K10 KIWI HARVEST | Auckland | MWES K10 | 2025-01-04 | 45661.4146 | 2025-01-04 | 45661.5479 | 0.0095464 | 0.00015495 | 97 | 5976 | Unplanned | Defective equipment
2849 |  | 37157 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-01-04 | 45661.4375 | 2025-01-04 | 45661.5042 | 0.0070544 | 7.3477e-05 | 46 | 4416 | Unplanned | Defective equipment
2850 |  | 37158 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2025-01-04 | 45661.2931 | 2025-01-04 | 45661.4653 | 0.00079234 | 3.195e-06 | 2 | 496 | Unplanned | Vegetation
2851 |  | 37159 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-01-04 | 45661.5049 | 2025-01-04 | 45661.5875 | 0.0020911 | 1.7572e-05 | 11 | 1309 | Unplanned | Cause unknown
2852 |  | 37160 | BMON K10 - K10 NORTHBORO ROAD | Northern | BMON K10 | 2025-01-04 | 45661.9049 | 2025-01-04 | 45661.95 | 0.074761 | 0.0011502 | 720 | 46800 | Unplanned | Cause unknown
2853 |  | 37162 | HOBV K11 - K11 TRIG RD +LS | Northern | HOBV K11 | 2025-01-06 | 45663.1625 | 2025-01-06 | 45663.1708 | 0.0055592 | 0.00046326 | 290 | 3480 | Unplanned | Defective equipment
2854 |  | 37163 | TPAP K16 - K16 MAYS RD | Auckland | TPAP K16 | 2025-01-06 | 45663.4563 | 2025-01-08 | 45665.5167 | 0.0094793 | 3.195e-06 | 2 | 5934 | Unplanned | Defective equipment
2855 |  | 37166 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2025-01-06 | 45663.9076 | 2025-01-06 | 45663.9688 | 0.0043579 | 4.9519e-05 | 31 | 2728 | Unplanned | Wildlife
2856 |  | 37167 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-01-06 | 45663.9035 | 2025-01-07 | 45664.3722 | 0.0021566 | 3.195e-06 | 2 | 1350 | Unplanned | Cause unknown
2857 |  | 37168 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2025-01-06 | 45663.9743 | 2025-01-07 | 45664.0639 | 0.00040256 | 3.195e-06 | 2 | 252 | Unplanned | Cause unknown
2858 |  | 37169 | MILF K03 - K03 KITCHENER ROAD | Northern | MILF K03 | 2025-01-07 | 45664.0882 | 2025-01-07 | 45664.4167 | 0.0080927 | 5.4314e-05 | 17 | 5066 | Unplanned | Defective equipment
2859 |  | 37170 | WSWA K06 - K06 ROSKILL RIPPLE | Auckland | WSWA K06 | 2025-01-07 | 45664.5458 | 2025-01-07 | 45664.7743 | 0.25037 | 0.0029873 | 1551 | 156731 | Unplanned | Defective equipment
2860 |  | 37172 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-01-07 | 45664.7396 | 2025-01-07 | 45664.7917 | 0.00023962 | 3.194e-06 | 2 | 150 | Unplanned | Third party interference
2861 |  | 37173 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2025-01-07 | 45664.7194 | 2025-01-07 | 45664.9826 | 0.00060544 | 1.597e-06 | 1 | 379 | Unplanned | Vegetation
2862 |  | 37174 | BUSH K01 - K01 WILLIAM PICKERING | Northern | BUSH K01 | 2025-01-08 | 45665.2917 | 2025-01-08 | 45665.5521 | 0.0011981 | 3.195e-06 | 2 | 750 | Unplanned | Defective equipment
2863 |  | 37177 | MANU K04 - K04 CENTRE WEYMOUTH RD VIA LS | Auckland | MANU K04 | 2025-01-09 | 45666.4375 | 2025-01-09 | 45666.6833 | 0.15105 | 0.00080033 | 358 | 94557 | Unplanned | Third party interference
2864 |  | 37178 | ORAK K05 - K05 GODDEN CRES | Auckland | ORAK K05 | 2025-01-09 | 45666.4076 | 2025-01-09 | 45666.7583 | 0.065344 | 0.00012939 | 81 | 40905 | Planned | Planned
2865 |  | 37179 | GULF K05 - K05 ALEC CRAIG WAY | Northern | GULF K05 | 2025-01-09 | 45666.5104 | 2025-01-09 | 45666.5799 | 0.00095848 | 9.584e-06 | 6 | 600 | Unplanned | Defective equipment
2866 |  | 37180 | RIVE K08 - K08 ACCESS RD | Northern | RIVE K08 | 2025-01-09 | 45666.7646 | 2025-01-09 | 45666.7833 | 4.3131e-05 | 1.598e-06 | 1 | 27 | Unplanned | Third party interference
2867 |  | 37180 | RIVE K08 - K08 ACCESS RD | Northern | RIVE K09 | 2025-01-09 | 45666.7646 | 2025-01-09 | 45666.7833 | 0.024154 | 0.0022141 | 1386 | 15120 | Unplanned | Third party interference
2868 |  | 37183 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2025-01-10 | 45667.3542 | 2025-01-10 | 45667.6215 | 0.00061502 | 1.597e-06 | 1 | 385 | Planned | Planned
2869 |  | 37184 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2025-01-10 | 45667.4181 | 2025-01-10 | 45667.7201 | 0.27726 | 0.00063739 | 399 | 173565 | Planned | Planned
2870 |  | 37185 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-01-10 | 45667.8375 | 2025-01-10 | 45667.9278 | 0.00020767 | 1.597e-06 | 1 | 130 | Unplanned | Cause unknown
2871 |  | 37186 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2025-01-11 | 45668.0382 | 2025-01-11 | 45668.1743 | 0.018553 | 0.00061184 | 383 | 11614 | Unplanned | Defective equipment
2872 |  | 37187 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-01-11 | 45668.6819 | 2025-01-11 | 45668.9965 | 0.0021709 | 4.792e-06 | 3 | 1359 | Unplanned | Third party interference
2873 |  | 37189 | ONEH K02 - K02 - GALWAY ST | Auckland | ONEH K02 | 2025-01-12 | 45669.3361 | 2025-01-12 | 45669.7014 | 0.00084026 | 1.597e-06 | 1 | 526 | Planned | Planned
2874 |  | 37190 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-12 | 45669.2493 | 2025-01-12 | 45669.3472 | 0.00045048 | 3.195e-06 | 2 | 282 | Unplanned | Wildlife
2875 |  | 37192 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-01-12 | 45669.6431 | 2025-01-12 | 45669.7153 | 0.0021598 | 2.0766e-05 | 13 | 1352 | Unplanned | Wildlife
2876 |  | 37193 | KING K01 - K01 DOMINION RD | Auckland | KING K01 | 2025-01-13 | 45670.3875 | 2025-01-13 | 45670.3903 | 0.0070288 | 0.0017572 | 1100 | 4400 | Unplanned | Defective equipment
2877 |  | 37193 | KING K01 - K01 DOMINION RD | Auckland | KING K10 | 2025-01-13 | 45670.3875 | 2025-01-13 | 45670.3903 | 0.0043068 | 0.0010767 | 674 | 2696 | Unplanned | Defective equipment
2878 |  | 37194 | BAIR K10 - K10 BAIRDS ROAD EAST | Auckland | BAIR K10 | 2025-01-13 | 45670.5368 | 2025-01-13 | 45670.5868 | 0.0072461 | 0.00010064 | 63 | 4536 | Unplanned | Cause unknown
2879 |  | 37195 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2025-01-13 | 45670.6993 | 2025-01-13 | 45670.7674 | 0.003131 | 3.1949e-05 | 20 | 1960 | Unplanned | Wildlife
2880 |  | 37197 | SIMP K08 - K08 SEIBEL ROAD | Northern | SIMP K08 | 2025-01-14 | 45671.1597 | 2025-01-14 | 45671.2035 | 0.11865 | 0.0018834 | 1179 | 74277 | Unplanned | Wildlife
2881 |  | 37198 | SPUR K03 - K03 WADE RIVER | Northern | SPUR K03 | 2025-01-14 | 45671.7243 | 2025-01-14 | 45671.7326 | 1.917e-05 | 1.597e-06 | 1 | 12 | Unplanned | Other Cause | Outage caused by Tap Operation
2882 |  | 37202 | SPUR K09 - K09 PANORAMA | Northern | SPUR K07 | 2025-01-14 | 45671.9479 | 2025-01-14 | 45671.9514 | 0.0015479 | 0.00051598 | 323 | 969 | Unplanned | Defective equipment
2883 |  | 37202 | SPUR K09 - K09 PANORAMA | Northern | SPUR K09 | 2025-01-14 | 45671.9479 | 2025-01-14 | 45671.9514 | 0.001246 | 0.00024919 | 156 | 780 | Unplanned | Defective equipment
2884 |  | 37203 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-01-14 | 45671.8757 | 2025-01-14 | 45671.9493 | 0.0045719 | 4.3131e-05 | 27 | 2862 | Unplanned | Cause unknown
2885 |  | 37204 | NEWM K30 - K30 BP CROWHURST ST | Auckland | NEWM K30 | 2025-01-14 | 45671.9236 | 2025-01-15 | 45672.1306 | 0.016185 | 5.4314e-05 | 34 | 10132 | Planned | Planned
2886 |  | 37206 | ONEH K06 - K06 - SELWYN ST NORTH | Auckland | ONEH K06 | 2025-01-15 | 45672.2201 | 2025-01-15 | 45672.2479 | 0.027349 | 0.00068371 | 428 | 17120 | Planned | Planned
2887 |  | 37207 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-01-15 | 45672.2486 | 2025-01-15 | 45672.5125 | 0.021122 | 0.00015175 | 95 | 13222 | Unplanned | Wildlife
2888 |  | 37208 | MKAU K07 - K07 TE IRIRANGI DRIVE | Auckland | MKAU K07 | 2025-01-15 | 45672.3347 | 2025-01-15 | 45672.3903 | 0.00051119 | 6.389e-06 | 4 | 320 | Planned | Planned
2889 |  | 37209 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-01-15 | 45672.3347 | 2025-01-15 | 45672.6868 | 0.021932 | 4.9514e-05 | 31 | 13729 | Planned | Planned
2890 |  | 37210 | TPAP K16 - K16 MAYS RD | Auckland | TPAP K16 | 2025-01-15 | 45672.3958 | 2025-01-15 | 45672.4264 | 0.0024601 | 5.5911e-05 | 35 | 1540 | Planned | Planned
2891 |  | 37211 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-01-15 | 45672.4889 | 2025-01-15 | 45672.5069 | 0.003032 | 0.00011661 | 73 | 1898 | Unplanned | Defective equipment
2892 |  | 37212 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2025-01-15 | 45672.5958 | 2025-01-15 | 45672.6319 | 0.0015783 | 3.0352e-05 | 19 | 988 | Unplanned | Defective equipment
2893 |  | 37213 | WARK K08 - K08 GOLF | Northern | WARK K08 | 2025-01-15 | 45672.041 | 2025-01-16 | 45673.1931 | 0.071555 | 4.3131e-05 | 27 | 44793 | Unplanned | Defective equipment
2894 |  | 37215 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2025-01-16 | 45673.1472 | 2025-01-16 | 45673.1701 | 0.0027412 | 8.3067e-05 | 52 | 1716 | Unplanned | Vegetation
2895 |  | 37217 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-01-16 | 45673.3562 | 2025-01-16 | 45673.641 | 0.00065496 | 1.597e-06 | 1 | 410 | Planned | Planned
2896 |  | 37218 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-16 | 45673.3542 | 2025-01-16 | 45673.7174 | 0.024229 | 4.6325e-05 | 29 | 15167 | Planned | Planned
2897 |  | 37219 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-01-16 | 45673.3549 | 2025-01-16 | 45673.7396 | 0.077234 | 0.00027797 | 126 | 48348 | Planned | Planned
2898 |  | 37220 | ONEH K08 - K08 - TAWA RD | Auckland | ONEH K08 | 2025-01-16 | 45673.4347 | 2025-01-16 | 45673.5493 | 0.051723 | 0.00076039 | 476 | 32378 | Planned | Planned
2899 |  | 37221 | RBEA - Red Beach | Northern | RBEA K10 | 2025-01-16 | 45673.5167 | 2025-01-16 | 45673.5201 | 0.0053914 | 0.0010783 | 675 | 3375 | Unplanned | Human error
2900 |  | 37221 | RBEA - Red Beach | Northern | RBEA K11 | 2025-01-16 | 45673.5167 | 2025-01-16 | 45673.5201 | 0.0043611 | 0.00087223 | 546 | 2730 | Unplanned | Human error
2901 |  | 37221 | RBEA - Red Beach | Northern | RBEA K13 | 2025-01-16 | 45673.5167 | 2025-01-16 | 45673.5201 | 9.585e-05 | 2.3955e-05 | 15 | 60 | Unplanned | Human error
2902 |  | 37223 | NEWM K02 - K02 BROADWAY CENTRE | Auckland | NEWM K02 | 2025-01-16 | 45673.6486 | 2025-01-17 | 45674.1743 | 0.079812 | 0.00010543 | 66 | 49962 | Unplanned | Third party interference
2903 |  | 37224 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-16 | 45673.5479 | 2025-01-16 | 45673.6882 | 0.0058084 | 2.8754e-05 | 18 | 3636 | Unplanned | Defective equipment
2904 |  | 37226 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-01-16 | 45673.6472 | 2025-01-17 | 45674.7083 | 0.0024409 | 1.597e-06 | 1 | 1528 | Unplanned | Defective equipment
2905 |  | 37227 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-17 | 45674.2694 | 2025-01-17 | 45674.3264 | 0.00065496 | 7.987e-06 | 5 | 410 | Unplanned | Cause unknown
2906 |  | 37228 | RBEA K06 - K06 VIPOND RD | Northern | RBEA K06 | 2025-01-17 | 45674.3542 | 2025-01-17 | 45674.7153 | 0.07393 | 0.00014217 | 89 | 46280 | Planned | Planned
2907 |  | 37229 | TATA K04 - K04 HARBOUR VIEW | Northern | TATA K04 | 2025-01-17 | 45674.375 | 2025-01-17 | 45674.6583 | 0.093854 | 0.00023003 | 144 | 58752 | Planned | Planned
2908 |  | 37230 | BAIR K10 - K10 BAIRDS ROAD EAST | Auckland | BAIR K10 | 2025-01-17 | 45674.7021 | 2025-01-17 | 45674.75 | 0.0069442 | 0.00010064 | 63 | 4347 | Unplanned | Third party interference
2909 |  | 37233 | WGAT K11 - K11 HOLMES | Northern | WGAT K11 | 2025-01-18 | 45675.3542 | 2025-01-18 | 45675.6715 | 0.088335 | 0.00019329 | 121 | 55297 | Planned | Planned
2910 |  | 37234 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-01-18 | 45675.2806 | 2025-01-18 | 45675.4861 | 0.0040416 | 3.0353e-05 | 19 | 2530 | Unplanned | Vegetation
2911 |  | 37235 | ONEH K08 - K08 - TAWA RD | Auckland | ONEH K08 | 2025-01-18 | 45675.375 | 2025-01-18 | 45675.7292 | 0.27293 | 0.00053515 | 335 | 170850 | Planned | Planned
2912 |  | 37236 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2025-01-18 | 45675.4076 | 2025-01-18 | 45675.6479 | 0.037585 | 0.00010863 | 68 | 23528 | Planned | Planned
2913 |  | 37237 | WARK K04 - K04 LIME WORKS | Northern | SNEL K08 | 2025-01-18 | 45675.6458 | 2025-01-18 | 45675.7035 | 0.0069681 | 0.0011614 | 727 | 4362 | Unplanned | Cause unknown
2914 |  | 37237 | WARK K04 - K04 LIME WORKS | Northern | SNEL K10 | 2025-01-18 | 45675.6458 | 2025-01-18 | 45675.7035 | 0.0065464 | 0.0010911 | 683 | 4098 | Unplanned | Cause unknown
2915 |  | 37237 | WARK K04 - K04 LIME WORKS | Northern | SNEL K11 | 2025-01-18 | 45675.6458 | 2025-01-18 | 45675.7035 | 0.00089458 | 0.00012781 | 80 | 560 | Unplanned | Cause unknown
2916 |  | 37237 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2025-01-18 | 45675.6458 | 2025-01-18 | 45675.7035 | 0.010898 | 0.00029072 | 106 | 6822 | Unplanned | Cause unknown
2917 |  | 37238 | ATKI K11 - K11 PLEASANT RD | Northern | ATKI K11 | 2025-01-18 | 45675.8319 | 2025-01-18 | 45675.8333 | 0.0019936 | 0.00099682 | 624 | 1248 | Unplanned | Third party interference
2918 |  | 37239 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-18 | 45675.8118 | 2025-01-18 | 45675.8819 | 0.0029042 | 2.8754e-05 | 18 | 1818 | Unplanned | Defective equipment
2919 |  | 37241 | PAPA K06 - K06 13 PORCHESTER RD | Auckland | PAPA K06 | 2025-01-19 | 45676.134 | 2025-01-19 | 45676.2021 | 0.0089234 | 9.1055e-05 | 57 | 5586 | Unplanned | Vegetation
2920 |  | 37242 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2025-01-19 | 45676.3778 | 2025-01-19 | 45676.7778 | 0.012882 | 2.2364e-05 | 14 | 8064 | Unplanned | Cause unknown
2921 |  | 37243 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2025-01-19 | 45676.4764 | 2025-01-20 | 45677.0097 | 0.13506 | 0.00077636 | 486 | 84544 | Unplanned | Third party interference
2922 |  | 37244 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2025-01-19 | 45676.8611 | 2025-01-20 | 45677.4604 | 0.31016 | 0.001663 | 444 | 194159 | Unplanned | Vegetation
2923 |  | 37245 | PAPA K06 - K06 13 PORCHESTER RD | Auckland | PAPA K06 | 2025-01-19 | 45676.9174 | 2025-01-20 | 45677.2132 | 0.090942 | 0.00029873 | 187 | 56929 | Planned | Planned
2924 |  | 37246 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-20 | 45677.1667 | 2025-01-20 | 45677.2347 | 0.014355 | 0.00015176 | 95 | 8986 | Planned | Planned
2925 |  | 37247 | NSBT55A - TP SILVERDALE 2842 - P899 (55A) | Northern | MANL K02 | 2025-01-20 | 45677.4812 | 2025-01-20 | 45677.8542 | 0.28143 | 0.0015607 | 700 | 176173 | Unplanned | Defective equipment
2926 |  | 37248 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2025-01-20 | 45677.5181 | 2025-01-20 | 45677.5625 | 0.00092014 | 1.4377e-05 | 9 | 576 | Unplanned | Wildlife
2927 |  | 37249 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-01-20 | 45677.5132 | 2025-01-20 | 45677.6583 | 0.0040064 | 1.917e-05 | 12 | 2508 | Unplanned | Vegetation
2928 |  | 37250 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-01-20 | 45677.8417 | 2025-01-21 | 45678.1125 | 0.002492 | 6.39e-06 | 4 | 1560 | Unplanned | Defective equipment
2929 |  | 37251 | NEWT K19 - K19 JOHN ANDREW | Auckland | NEWT K19 | 2025-01-20 | 45677.9583 | 2025-01-21 | 45678.2743 | 0.10321 | 0.00022684 | 142 | 64610 | Planned | Planned
2930 |  | 37256 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2025-01-21 | 45678.2486 | 2025-01-21 | 45678.6111 | 0.068767 | 0.00087705 | 384 | 43048 | Unplanned | Vegetation
2931 |  | 37257 | NSBT59 - WELLSFORD H02 - WARKWORTH P284 (59) | Northern | WARK K13 | 2025-01-21 | 45678.2542 | 2025-01-21 | 45678.6278 | 0.062197 | 0.0019664 | 1231 | 38935 | Unplanned | Vegetation
2932 |  | 37258 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-01-21 | 45678.3236 | 2025-01-21 | 45678.4014 | 0.01532 | 0.00021726 | 136 | 9590 | Unplanned | Vegetation
2933 |  | 37261 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2025-01-21 | 45678.3562 | 2025-01-21 | 45678.6653 | 0.10645 | 0.00053675 | 305 | 66638 | Unplanned | Defective equipment
2934 |  | 37262 | LIVE J17 - J17 WAKEFIELD ST CAR PARK | Auckland | LIVE J17 | 2025-01-21 | 45678.2882 | 2025-01-21 | 45678.3646 | 0.0019329 | 1.7572e-05 | 11 | 1210 | Unplanned | Third party interference
2935 |  | 37263 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2025-01-21 | 45678.3542 | 2025-01-21 | 45678.6354 | 0.40759 | 0.0010064 | 630 | 255150 | Planned | Planned
2936 |  | 37264 | TATA K11 - K11 YEOVIL ROAD | Northern | TATA K08 | 2025-01-21 | 45678.3757 | 2025-01-21 | 45678.5528 | 0.041061 | 0.00016294 | 102 | 25704 | Planned | Planned
2937 |  | 37264 | TATA K11 - K11 YEOVIL ROAD | Northern | TATA K11 | 2025-01-21 | 45678.3757 | 2025-01-21 | 45678.5528 | 0.038698 | 0.00015176 | 95 | 24225 | Planned | Planned
2938 |  | 37265 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-21 | 45678.375 | 2025-01-21 | 45678.6681 | 0.0067413 | 1.5975e-05 | 10 | 4220 | Planned | Planned
2939 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | COAT K11 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.06621 | 0.0011262 | 705 | 41447 | Unplanned | Cause unknown
2940 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K02 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.0037764 | 0.00062939 | 394 | 2364 | Unplanned | Cause unknown
2941 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K03 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.0030671 | 0.00051118 | 320 | 1920 | Unplanned | Cause unknown
2942 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K05 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.0081758 | 0.0013626 | 853 | 5118 | Unplanned | Cause unknown
2943 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K06 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.003556 | 0.00059265 | 371 | 2226 | Unplanned | Cause unknown
2944 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K08 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.0063739 | 0.0010623 | 665 | 3990 | Unplanned | Cause unknown
2945 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM K09 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 0.019821 | 0.0033035 | 2068 | 12408 | Unplanned | Cause unknown
2946 |  | 37267 | NSBT93A - COATESVILLE H01 - RIVERHEAD H02 (93A) | Northern | WAIM LS | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.8236 | 9.585e-06 | 1.597e-06 | 1 | 6 | Unplanned | Cause unknown
2947 |  | 37268 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K06 | 2025-01-21 | 45678.3979 | 2025-01-21 | 45678.7493 | 0.00083867 | 4.792e-06 | 3 | 525 | Unplanned | Defective equipment
2948 |  | 37268 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-01-21 | 45678.3979 | 2025-01-21 | 45678.7493 | 0.18204 | 0.0033035 | 2068 | 113954 | Unplanned | Defective equipment
2949 |  | 37269 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2025-01-21 | 45678.4354 | 2025-01-21 | 45678.4757 | 0.081774 | 0.0029122 | 1823 | 51190 | Unplanned | Cause unknown
2950 |  | 37270 | ESL 287F KKAP K03 - 287F | Northern | KKAP K03 | 2025-01-21 | 45678.3896 | 2025-01-21 | 45678.625 | 0.044948 | 0.00013259 | 83 | 28137 | Unplanned | Vegetation
2951 |  | 37273 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2025-01-21 | 45678.4951 | 2025-01-21 | 45678.7681 | 0.10337 | 0.001778 | 898 | 64712 | Unplanned | Defective equipment
2952 |  | 37273 | COAT K03 - K03 SCREEN ROAD | Northern | SPUR K02 | 2025-01-21 | 45678.4951 | 2025-01-21 | 45678.7681 | 0.00070288 | 1.7571e-05 | 11 | 440 | Unplanned | Defective equipment
2953 |  | 37277 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-01-21 | 45678.5361 | 2025-01-21 | 45678.6431 | 0.056975 | 0.00037222 | 233 | 35666 | Unplanned | Cause unknown
2954 |  | 37288 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2025-01-21 | 45678.5104 | 2025-01-21 | 45678.7146 | 0.021265 | 8.3072e-05 | 52 | 13312 | Unplanned | Vegetation
2955 |  | 37288 | MANU K12 - K12 ALFRISTON RD | Auckland | TAKA K12 | 2025-01-21 | 45678.5104 | 2025-01-21 | 45678.7146 | 0.003639 | 4.1538e-05 | 26 | 2278 | Unplanned | Vegetation
2956 |  | 37291 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-01-21 | 45678.5035 | 2025-01-21 | 45678.634 | 0.00060064 | 3.194e-06 | 2 | 376 | Unplanned | Cause unknown
2957 |  | 37292 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-01-21 | 45678.6542 | 2025-01-21 | 45678.7778 | 0.05651 | 0.00037222 | 233 | 35375 | Unplanned | Vegetation
2958 |  | 37293 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-01-21 | 45678.3354 | 2025-01-21 | 45678.6951 | 0.005794 | 4.1534e-05 | 13 | 3627 | Unplanned | Vegetation
2959 |  | 37294 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2025-01-21 | 45678.4854 | 2025-01-21 | 45678.7951 | 0.0021374 | 4.792e-06 | 3 | 1338 | Unplanned | Defective equipment
2960 |  | 37295 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2025-01-21 | 45678.784 | 2025-01-21 | 45678.8618 | 0.021649 | 0.00019329 | 121 | 13552 | Unplanned | Defective equipment
2961 |  | 37296 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-01-21 | 45678.9708 | 2025-01-22 | 45679.0292 | 0.0060384 | 7.1884e-05 | 45 | 3780 | Unplanned | Vegetation
2962 |  | 37298 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-22 | 45679.3354 | 2025-01-22 | 45679.6479 | 0.0014297 | 3.195e-06 | 2 | 895 | Planned | Planned
2963 |  | 37299 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-01-22 | 45679.3542 | 2025-01-22 | 45679.6931 | 0.041317 | 8.4659e-05 | 53 | 25864 | Planned | Planned
2964 |  | 37301 | HELE K03 - K03 MAKIRI | Northern | HELE K03 | 2025-01-22 | 45679.4854 | 2025-01-22 | 45679.5799 | 0.0043451 | 3.1949e-05 | 20 | 2720 | Unplanned | Defective equipment
2965 |  | 37303 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-01-22 | 45679.6347 | 2025-01-23 | 45680.0097 | 0.016677 | 9.4251e-05 | 59 | 10440 | Unplanned | Defective equipment
2966 |  | 37305 | LAIN K02 - K02 WAIMA RD | Northern | LAIN K02 | 2025-01-22 | 45679.6972 | 2025-01-22 | 45679.7403 | 0.043876 | 0.00070767 | 443 | 27466 | Unplanned | Vegetation
2967 |  | 37306 | SPUR K07 - K07 PINEVALLEY | Northern | SPUR K07 | 2025-01-22 | 45679.9104 | 2025-01-22 | 45679.9424 | 0.0049969 | 0.00010863 | 68 | 3128 | Unplanned | Third party interference
2968 |  | 37307 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-01-23 | 45680.2104 | 2025-01-23 | 45680.7472 | 0.036857 | 0.0023037 | 721 | 23072 | Planned | Planned
2969 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K02 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.00048882 | 0.00024441 | 153 | 306 | Unplanned | Cause unknown
2970 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K03 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0046071 | 0.0023035 | 1442 | 2884 | Unplanned | Cause unknown
2971 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K04 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.00060703 | 0.00030352 | 190 | 380 | Unplanned | Cause unknown
2972 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K05 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0036262 | 0.0018131 | 1135 | 2270 | Unplanned | Cause unknown
2973 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K06 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.00076039 | 0.0003802 | 238 | 476 | Unplanned | Cause unknown
2974 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K10 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.00020767 | 0.00010383 | 65 | 130 | Unplanned | Cause unknown
2975 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K11 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0013802 | 0.0006901 | 432 | 864 | Unplanned | Cause unknown
2976 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K12 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.001508 | 0.000754 | 472 | 944 | Unplanned | Cause unknown
2977 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K13 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0056646 | 0.0028323 | 1773 | 3546 | Unplanned | Cause unknown
2978 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL K14 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.00040256 | 0.00020128 | 126 | 252 | Unplanned | Cause unknown
2979 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | HVAL LS | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0 | 0 | 0 | 0 | Unplanned | Cause unknown
2980 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | KEEL K06 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0079458 | 0.0013243 | 829 | 4974 | Unplanned | Cause unknown
2981 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | KEEL K07 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0012939 | 0.00021566 | 135 | 810 | Unplanned | Cause unknown
2982 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | KEEL K10 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 9.585e-06 | 1.598e-06 | 1 | 6 | Unplanned | Cause unknown
2983 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | KEEL K11 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0089522 | 0.001492 | 934 | 5604 | Unplanned | Cause unknown
2984 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | KEEL K12 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.010812 | 0.001802 | 1128 | 6768 | Unplanned | Cause unknown
2985 |  | 37308 | NSBT38 - TP HEPBURN RD 2232 - WAIKAUKAU P500 (38) | Northern | KEEL K13 | 2025-01-23 | 45680.2181 | 2025-01-29 | 45686.1264 | 0.0037668 | 0.00062781 | 393 | 2358 | Unplanned | Cause unknown
2986 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K01 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0051885 | 0.0012971 | 812 | 3248 | Unplanned | Wildlife
2987 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K02 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0 | 0 | 0 | 0 | Unplanned | Wildlife
2988 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K04 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.006409 | 0.0016023 | 1003 | 4012 | Unplanned | Wildlife
2989 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K07 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 6.389e-05 | 1.598e-05 | 10 | 40 | Unplanned | Wildlife
2990 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K08 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0059106 | 0.0014777 | 925 | 3700 | Unplanned | Wildlife
2991 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K10 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0026773 | 0.00066934 | 419 | 1676 | Unplanned | Wildlife
2992 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HOBV K11 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.001853 | 0.00046329 | 290 | 1160 | Unplanned | Wildlife
2993 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K01 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 4.792e-06 | 1.597e-06 | 1 | 3 | Unplanned | Wildlife
2994 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K02 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0052956 | 0.0017652 | 1105 | 3315 | Unplanned | Wildlife
2995 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K03 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 2.8752e-05 | 9.582e-06 | 6 | 18 | Unplanned | Wildlife
2996 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K04 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.003647 | 0.0012157 | 761 | 2283 | Unplanned | Wildlife
2997 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K06 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0089378 | 0.0029793 | 1865 | 5595 | Unplanned | Wildlife
2998 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K07 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0048211 | 0.001607 | 1006 | 3018 | Unplanned | Wildlife
2999 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K09 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0025927 | 0.00086423 | 541 | 1623 | Unplanned | Wildlife
3000 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K10 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0064074 | 0.0021358 | 1337 | 4011 | Unplanned | Wildlife
3001 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K12 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.0013035 | 0.00043451 | 272 | 816 | Unplanned | Wildlife
3002 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K13 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 0.001893 | 0.00063099 | 395 | 1185 | Unplanned | Wildlife
3003 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K14 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 4.792e-06 | 1.597e-06 | 1 | 3 | Unplanned | Wildlife
3004 |  | 37309 | NSBT27 - TP HENDERSON 2332 - HOBSONVILLE L1 P232 (27) | Northern | HPOI K15 | 2025-01-23 | 45680.2562 | 2025-01-23 | 45680.3493 | 4.792e-06 | 1.597e-06 | 1 | 3 | Unplanned | Wildlife
3005 |  | 37310 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-23 | 45680.2917 | 2025-01-23 | 45680.6451 | 0.0017971 | 7.1885e-05 | 45 | 1125 | Planned | Planned
3006 |  | 37311 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-01-23 | 45680.3333 | 2025-01-23 | 45680.7125 | 0.038377 | 7.0287e-05 | 44 | 24024 | Planned | Planned
3007 |  | 37312 | NLYN K10 - K10 MARGAN AVE | Northern | NLYN K10 | 2025-01-23 | 45680.3681 | 2025-01-23 | 45680.7465 | 0.069649 | 0.0001278 | 80 | 43600 | Planned | Planned
3008 |  | 37313 | HCRE K02 - K02 FOWLER STREET | Northern | HCRE K02 | 2025-01-23 | 45680.3833 | 2025-01-23 | 45680.6042 | 0.032004 | 0.00010064 | 63 | 20034 | Planned | Planned
3009 |  | 37315 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-01-23 | 45680.3417 | 2025-01-23 | 45680.5049 | 0.0003754 | 1.597e-06 | 1 | 235 | Unplanned | Vegetation
3010 |  | 37316 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2025-01-23 | 45680.559 | 2025-01-23 | 45680.6111 | 0.00047924 | 6.389e-06 | 4 | 300 | Unplanned | Defective equipment
3011 |  | 37317 | WAIH K02 - K02 OSTEND RD | Auckland | WAIH K02 | 2025-01-23 | 45680.7674 | 2025-01-23 | 45680.7819 | 0.00046965 | 2.2364e-05 | 14 | 294 | Unplanned | Defective equipment
3012 |  | 37318 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2025-01-23 | 45680.8472 | 2025-01-23 | 45680.8569 | 0.0053675 | 0.00038339 | 240 | 3360 | Unplanned | Defective equipment
3013 |  | 37319 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2025-01-23 | 45680.7833 | 2025-01-23 | 45680.8542 | 0.0026071 | 2.5559e-05 | 16 | 1632 | Unplanned | Wildlife
3014 |  | 37320 | NEWM K30 - K30 BP CROWHURST ST | Auckland | NEWM K30 | 2025-01-23 | 45680.9174 | 2025-01-24 | 45681.0347 | 0.009179 | 5.4314e-05 | 34 | 5746 | Planned | Planned
3015 |  | 37321 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-01-24 | 45681.3368 | 2025-01-24 | 45681.4792 | 0.027181 | 0.00013259 | 83 | 17015 | Planned | Planned
3016 |  | 37322 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-24 | 45681.3125 | 2025-01-24 | 45681.5986 | 0.002623 | 6.39e-06 | 4 | 1642 | Planned | Planned
3017 |  | 37323 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-01-24 | 45681.375 | 2025-01-24 | 45681.8285 | 0.26913 | 0.00041214 | 258 | 168474 | Planned | Planned
3018 |  | 37325 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-01-24 | 45681.3542 | 2025-01-24 | 45681.6389 | 0.00065496 | 1.597e-06 | 1 | 410 | Planned | Planned
3019 |  | 37327 | TAKA K13 - K13 COSGROVE RD | Auckland | TAKA K13 | 2025-01-24 | 45681.5201 | 2025-01-24 | 45681.8576 | 0.28335 | 0.0011118 | 696 | 177375 | Unplanned | Third party interference
3020 |  | 37328 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-01-24 | 45681.391 | 2025-01-24 | 45681.609 | 0.0020064 | 6.389e-06 | 4 | 1256 | Unplanned | Defective equipment
3021 |  | 37329 | VICT K22 - K22 QUEEN STREET (MERCURY) | Auckland | VICT K22 | 2025-01-24 | 45681.6014 | 2025-01-24 | 45681.6972 | 0.11024 | 0.00088979 | 557 | 69007 | Unplanned | Defective equipment
3022 |  | 37330 | NEWT K25 - K25 KYBER PASS RD EDEN HOUSE VIA LS | Auckland | NEWM K06 | 2025-01-24 | 45681.6167 | 2025-01-24 | 45681.8229 | 0.018641 | 0.0005064 | 317 | 11669 | Unplanned | Defective equipment
3023 |  | 37330 | NEWT K25 - K25 KYBER PASS RD EDEN HOUSE VIA LS | Auckland | NEWM K30 | 2025-01-24 | 45681.6167 | 2025-01-24 | 45681.8229 | 0.13225 | 0.0012189 | 478 | 82788 | Unplanned | Defective equipment
3024 |  | 37330 | NEWT K25 - K25 KYBER PASS RD EDEN HOUSE VIA LS | Auckland | NEWT K25 | 2025-01-24 | 45681.6167 | 2025-01-24 | 45681.8229 | 0.28936 | 0.0012205 | 657 | 181135 | Unplanned | Defective equipment
3025 |  | 37331 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2025-01-24 | 45681.5889 | 2025-01-29 | 45686.6736 | 0.023797 | 0.00016294 | 102 | 14897 | Unplanned | Defective equipment
3026 |  | 37332 | PONS K11 - K11 FARRAR ST | Auckland | PONS K11 | 2025-01-24 | 45681.7521 | 2025-01-24 | 45681.9604 | 0.10804 | 0.00072206 | 452 | 67635 | Unplanned | Third party interference
3027 |  | 37333 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2025-01-24 | 45681.8354 | 2025-01-24 | 45681.9236 | 0.01197 | 9.4246e-05 | 59 | 7493 | Unplanned | Defective equipment
3028 |  | 37334 | VICT K20 - K20 MID CITY TOWERS | Auckland | VICT K20 | 2025-01-24 | 45681.6243 | 2025-01-24 | 45681.7639 | 0.00032109 | 1.597e-06 | 1 | 201 | Unplanned | Cause unknown
3029 |  | 37337 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2025-01-25 | 45682.4576 | 2025-01-25 | 45682.609 | 0.033083 | 0.00015176 | 95 | 20710 | Unplanned | Third party interference
3030 |  | 37339 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-01-25 | 45682.4014 | 2025-01-25 | 45682.5174 | 0.00053355 | 3.194e-06 | 2 | 334 | Unplanned | Vegetation
3031 |  | 37340 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-01-25 | 45682.4847 | 2025-01-25 | 45682.5903 | 0.00024281 | 1.597e-06 | 1 | 152 | Unplanned | Cause unknown
3032 |  | 37341 | HOWI K10 - K10 FINNERTY AVE | Auckland | HOWI K10 | 2025-01-25 | 45682.641 | 2025-01-25 | 45682.7097 | 0.19866 | 0.0020607 | 1290 | 124360 | Unplanned | Defective equipment
3033 |  | 37342 | BAIR K14 - K14 WYMONDLEY | Auckland | BAIR K14 | 2025-01-25 | 45682.6417 | 2025-01-25 | 45682.75 | 0.023924 | 0.00015336 | 96 | 14976 | Unplanned | Third party interference
3034 |  | 37345 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-01-25 | 45682.8257 | 2025-01-25 | 45682.8944 | 0.0094889 | 9.5847e-05 | 60 | 5940 | Unplanned | Vegetation
3035 |  | 37348 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-01-26 | 45683.1438 | 2025-01-26 | 45683.609 | 0.030813 | 0.00027796 | 136 | 19289 | Unplanned | Vegetation
3036 |  | 37349 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2025-01-26 | 45683.1111 | 2025-01-26 | 45683.3035 | 0.0531 | 0.0001917 | 120 | 33240 | Unplanned | Vegetation
3037 |  | 37352 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2025-01-26 | 45683.2701 | 2025-01-26 | 45683.5264 | 0.051678 | 0.00025879 | 162 | 32350 | Unplanned | Defective equipment
3038 |  | 37353 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2025-01-26 | 45683.0875 | 2025-01-26 | 45683.316 | 0.0089346 | 2.7157e-05 | 17 | 5593 | Unplanned | Vegetation
3039 |  | 37354 | MCEN K19 - K19 COCA COLA AMATIL | Auckland | MCEN K19 | 2025-01-26 | 45683.2792 | 2025-01-26 | 45683.7535 | 0.0021821 | 3.195e-06 | 2 | 1366 | Unplanned | Defective equipment
3040 |  | 37355 | NEWM K02 - K02 BROADWAY CENTRE | Auckland | NEWM K02 | 2025-01-26 | 45683.3694 | 2025-01-26 | 45683.4354 | 0.010016 | 0.00010543 | 66 | 6270 | Unplanned | Vegetation
3041 |  | 37356 | WSWA K12 - K12 WHITE SWAN RD | Auckland | WSWA K12 | 2025-01-26 | 45683.375 | 2025-01-26 | 45683.6806 | 0.013355 | 3.0351e-05 | 19 | 8360 | Planned | Planned
3042 |  | 37357 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2025-01-26 | 45683.3993 | 2025-01-26 | 45683.4563 | 0.038516 | 0.00048724 | 305 | 24111 | Unplanned | Vegetation
3043 |  | 37359 | KEEL K06 - K06 HICKORY AVE | Northern | KEEL K06 | 2025-01-26 | 45683.5889 | 2025-01-26 | 45683.7694 | 0.20668 | 0.0016422 | 829 | 129379 | Unplanned | Vegetation
3044 |  | 37360 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-26 | 45683.5986 | 2025-01-26 | 45683.6937 | 0.056435 | 0.00072364 | 312 | 35328 | Unplanned | Vegetation
3045 |  | 37362 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2025-01-26 | 45683.5514 | 2025-01-26 | 45683.7556 | 0.019438 | 8.3072e-05 | 52 | 12168 | Unplanned | Vegetation
3046 |  | 37362 | MANU K12 - K12 ALFRISTON RD | Auckland | TAKA K12 | 2025-01-26 | 45683.5514 | 2025-01-26 | 45683.7556 | 0.0060799 | 4.1538e-05 | 26 | 3806 | Unplanned | Vegetation
3047 |  | 37364 | WAIA K02 - K02 FIRTH ROAD | Northern | WAIA K02 | 2025-01-26 | 45683.7694 | 2025-01-26 | 45683.9722 | 0.10813 | 0.0015176 | 950 | 67690 | Unplanned | Vegetation
3048 |  | 37365 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2025-01-26 | 45683.7264 | 2025-01-26 | 45683.8611 | 0.00030991 | 1.597e-06 | 1 | 194 | Unplanned | Vegetation
3049 |  | 37366 | TORB K11 - K11 BEACH ROAD | Northern | TORB K11 | 2025-01-26 | 45683.7924 | 2025-01-26 | 45683.9444 | 0.059592 | 0.0031039 | 1943 | 37304 | Unplanned | Wildlife
3050 |  | 37367 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-01-26 | 45683.8882 | 2025-01-26 | 45683.9493 | 0.00056231 | 6.39e-06 | 4 | 352 | Unplanned | Vegetation
3051 |  | 37368 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2025-01-27 | 45684.1257 | 2025-01-27 | 45684.2431 | 0.06482 | 0.00085145 | 533 | 40577 | Unplanned | Vegetation
3052 |  | 37369 | MANU K07 - K07 HALVER RD | Auckland | MANU K07 | 2025-01-27 | 45684.275 | 2025-01-27 | 45684.6181 | 0.036959 | 0.00030991 | 120 | 23136 | Unplanned | Cause unknown
3053 |  | 37370 | SABU K08 - K08 GREAT NORTH RD | Northern | SABU K08 | 2025-01-27 | 45684.4444 | 2025-01-28 | 45685.4889 | 0.0048052 | 3.195e-06 | 2 | 3008 | Unplanned | Cause unknown
3054 |  | 37372 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2025-01-27 | 45684.6347 | 2025-01-27 | 45684.6667 | 0.01477 | 0.00032108 | 201 | 9246 | Unplanned | Vegetation
3055 |  | 37373 | GHIT K02 - K02 ORWELL RD | Northern | GHIT K02 | 2025-01-27 | 45684.7118 | 2025-01-27 | 45684.7514 | 0.054577 | 0.0018547 | 1161 | 34165 | Unplanned | Vegetation
3056 |  | 37374 | MANL K01 - K01 ARMY BAY | Northern | MANL K01 | 2025-01-28 | 45685.0285 | 2025-01-28 | 45685.0903 | 0.0059713 | 6.7093e-05 | 42 | 3738 | Unplanned | Defective equipment
3057 |  | 37375 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-01-28 | 45685.2139 | 2025-01-28 | 45685.7917 | 0.041882 | 0.003471 | 731 | 26218 | Planned | Planned
3058 |  | 37376 | NEWM K01 - K01 EDUCATIONAL DEPT VIA LS | Auckland | NEWM K01 | 2025-01-28 | 45685.3868 | 2025-01-28 | 45685.7201 | 0.058275 | 0.00012141 | 76 | 36480 | Planned | Planned
3059 |  | 37377 | SUNS K08 - K08 TARGET ROAD | Northern | SUNS K08 | 2025-01-28 | 45685.2424 | 2025-01-28 | 45685.3819 | 0.066787 | 0.00033227 | 208 | 41808 | Unplanned | Defective equipment
3060 |  | 37378 | NEWM K06 - K06 CARLTON GORE ROAD (111) | Auckland | NEWM K06 | 2025-01-28 | 45685.4576 | 2025-01-28 | 45685.5986 | 0.033627 | 0.00050639 | 317 | 21050 | Unplanned | Defective equipment
3061 |  | 37378 | NEWM K06 - K06 CARLTON GORE ROAD (111) | Auckland | NEWM K30 | 2025-01-28 | 45685.4576 | 2025-01-28 | 45685.5986 | 0.029138 | 0.00045527 | 285 | 18240 | Unplanned | Defective equipment
3062 |  | 37378 | NEWM K06 - K06 CARLTON GORE ROAD (111) | Auckland | NEWT K25 | 2025-01-28 | 45685.4576 | 2025-01-28 | 45685.5986 | 0.022083 | 0.00034505 | 216 | 13824 | Unplanned | Defective equipment
3063 |  | 37379 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-01-28 | 45685.3812 | 2025-01-28 | 45685.6583 | 0.004123 | 1.1181e-05 | 7 | 2581 | Planned | Planned
3064 |  | 37380 | RIVE K04 - K04 BARRETT RD | Northern | RIVE K04 | 2025-01-28 | 45685.3542 | 2025-01-28 | 45685.6653 | 0.002147 | 4.792e-06 | 3 | 1344 | Planned | Planned
3065 |  | 37381 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-01-28 | 45685.3576 | 2025-01-28 | 45685.7132 | 0.024537 | 4.7923e-05 | 30 | 15360 | Planned | Planned
3066 |  | 37382 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2025-01-28 | 45685.3958 | 2025-01-28 | 45685.6806 | 0.0013099 | 3.194e-06 | 2 | 820 | Planned | Planned
3067 |  | 37383 | COAT K06 - K06 GLENMORE ROAD | Northern | COAT K06 | 2025-01-28 | 45685.1618 | 2025-01-28 | 45685.25 | 0.00081151 | 6.39e-06 | 4 | 508 | Unplanned | Wildlife
3068 |  | 37384 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2025-01-28 | 45685.8201 | 2025-01-29 | 45686.5257 | 0.1358 | 0.00034985 | 219 | 85008 | Unplanned | Third party interference
3069 |  | 37385 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2025-01-28 | 45685.5743 | 2025-01-28 | 45685.7646 | 0.0004377 | 1.597e-06 | 1 | 274 | Unplanned | Wildlife
3070 |  | 37386 | BAIR K03 - K03 BAIRDS ROAD WEST VIA LS | Auckland | BAIR K03 | 2025-01-28 | 45685.8812 | 2025-01-28 | 45685.9854 | 0.15024 | 0.0010911 | 683 | 94052 | Unplanned | Defective equipment
3071 |  | 37386 | BAIR K03 - K03 BAIRDS ROAD WEST VIA LS | Auckland | BAIR K09 | 2025-01-28 | 45685.8812 | 2025-01-28 | 45685.9854 | 1.1181e-05 | 1.1181e-05 | 7 | 7 | Unplanned | Defective equipment
3072 |  | 37387 | MKAU K27 - K27 CARTER HOLT (VIA LST1) | Auckland | MKAU K27 | 2025-01-28 | 45685.9167 | 2025-01-29 | 45686.2 | 0.42625 | 0.0010447 | 654 | 266832 | Planned | Planned
3073 |  | 37388 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-01-28 | 45685.5771 | 2025-01-28 | 45685.8639 | 0.10371 | 0.00077157 | 483 | 64924 | Unplanned | Third party interference
3074 |  | 37389 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-01-29 | 45686.2146 | 2025-01-29 | 45686.8806 | 0.036962 | 0.0023356 | 731 | 23138 | Planned | Planned
3075 |  | 37390 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-29 | 45686.375 | 2025-01-29 | 45686.6958 | 0.030259 | 6.5496e-05 | 41 | 18942 | Planned | Planned
3076 |  | 37391 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2025-01-29 | 45686.3958 | 2025-01-29 | 45686.6111 | 0.0049521 | 1.5975e-05 | 10 | 3100 | Planned | Planned
3077 |  | 37392 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-01-29 | 45686.375 | 2025-01-29 | 45686.7188 | 0.014233 | 2.8754e-05 | 18 | 8910 | Planned | Planned
3078 |  | 37393 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2025-01-29 | 45686.4007 | 2025-01-29 | 45686.5167 | 0.034948 | 0.00020927 | 131 | 21877 | Planned | Planned
3079 |  | 38396 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-01-29 | 45686.5049 | 2025-01-29 | 45686.7361 | 0.020746 | 6.2296e-05 | 39 | 12987 | Unplanned | Third party interference
3080 |  | 38398 | DRIV K16 - K16 MANUKAU RD | Auckland | DRIV K16 | 2025-01-30 | 45687.0417 | 2025-01-30 | 45687.1396 | 0.042345 | 0.00030032 | 188 | 26508 | Planned | Planned
3081 |  | 38400 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-01-30 | 45687.2306 | 2025-01-30 | 45687.3132 | 0.0020911 | 1.7572e-05 | 11 | 1309 | Unplanned | Cause unknown
3082 |  | 38401 | WAIM K03 - K03 REWITI | Northern | WAIM K03 | 2025-01-30 | 45687.3333 | 2025-01-30 | 45687.6181 | 0.0019649 | 4.791e-06 | 3 | 1230 | Planned | Planned
3083 |  | 38402 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-01-30 | 45687.3556 | 2025-01-30 | 45687.7222 | 0.06694 | 0.00027797 | 126 | 41904 | Planned | Planned
3084 |  | 38403 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-01-30 | 45687.3861 | 2025-01-30 | 45687.4618 | 0.00034825 | 3.195e-06 | 2 | 218 | Unplanned | Cause unknown
3085 |  | 38404 | DRIV K05 - K05 ONSLOW AVE | Auckland | DRIV K05 | 2025-01-30 | 45687.4792 | 2025-01-30 | 45687.5417 | 0.020847 | 0.00023163 | 145 | 13050 | Unplanned | Defective equipment
3086 |  | 38405 | WAIM K03 - K03 REWITI | Northern | WAIM K03 | 2025-01-30 | 45687.3812 | 2025-01-30 | 45687.6799 | 0.007556 | 1.7572e-05 | 11 | 4730 | Planned | Planned
3087 |  | 38406 | HBUR K07 - K07 BIRKENHEAD AVE | Northern | HBUR K07 | 2025-01-30 | 45687.7986 | 2025-01-30 | 45687.8333 | 0.0064697 | 0.00012939 | 81 | 4050 | Unplanned | Defective equipment
3088 |  | 38407 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-01-30 | 45687.9 | 2025-01-30 | 45687.975 | 0.055644 | 0.00077157 | 483 | 34833 | Unplanned | Cause unknown
3089 |  | 38408 | WGAT K05 - K05 MAKI | Northern | WGAT K05 | 2025-01-30 | 45687.9167 | 2025-01-31 | 45688.0285 | 0.0051438 | 3.1949e-05 | 20 | 3220 | Planned | Planned
3090 |  | 38409 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-01-31 | 45688.209 | 2025-01-31 | 45688.7333 | 0.10393 | 0.0022445 | 763 | 65061 | Planned | Planned
3091 |  | 38410 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-01-31 | 45688.325 | 2025-01-31 | 45688.7111 | 0 | 0 | 0 | 0 | Planned | Planned
3092 |  | 38412 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2025-01-31 | 45688.3542 | 2025-01-31 | 45688.7396 | 0.03369 | 6.0703e-05 | 38 | 21090 | Planned | Planned
3093 |  | 38415 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-01-31 | 45688.4771 | 2025-01-31 | 45688.7188 | 0.046095 | 0.0010782 | 675 | 28855 | Unplanned | Vegetation
3094 |  | 38416 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-01-31 | 45688.5722 | 2025-01-31 | 45688.9618 | 0.050691 | 0.00039935 | 250 | 31732 | Unplanned | Vegetation
3095 |  | 38417 | SABU K08 - K08 GREAT NORTH RD | Northern | SABU K08 | 2025-01-31 | 45688.7882 | 2025-01-31 | 45688.816 | 0.0001278 | 3.195e-06 | 2 | 80 | Unplanned | Defective equipment
3096 |  | 38418 | KEEL K12 - K12 STURGES RD | Northern | KEEL K12 | 2025-01-31 | 45688.8264 | 2025-02-01 | 45689.0354 | 0.082704 | 0.00027476 | 172 | 51772 | Unplanned | Third party interference
3097 |  | 38419 | PAPA K09 - K09 LAURIE AVE | Auckland | PAPA K09 | 2025-02-01 | 45689.0646 | 2025-02-01 | 45689.2826 | 0.11236 | 0.00035783 | 224 | 70336 | Unplanned | Third party interference
3098 |  | 38420 | AVON K01 - K01 BLOCKHOUSE BAY RD.(353) | Auckland | AVON K01 | 2025-02-01 | 45689.0167 | 2025-02-01 | 45689.0819 | 0.12761 | 0.0032428 | 2030 | 79884 | Unplanned | Defective equipment
3099 |  | 38421 | NEWT K25 - K25 KYBER PASS RD EDEN HOUSE VIA LS | Auckland | NEWT K25 | 2025-02-01 | 45689.0833 | 2025-02-01 | 45689.1292 | 0.015709 | 0.00023802 | 149 | 9834 | Planned | Planned
3100 |  | 38422 | RANU K09 - K09 ALIDADE PLACE | Northern | RANU K09 | 2025-02-01 | 45689.2083 | 2025-02-02 | 45690.2326 | 0.0057572 | 0.00016933 | 53 | 3604 | Planned | Planned
3101 |  | 38423 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2025-02-01 | 45689.316 | 2025-02-01 | 45689.5722 | 0.033216 | 0.00025399 | 159 | 20793 | Unplanned | Third party interference
3102 |  | 38424 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-02-01 | 45689.5479 | 2025-02-01 | 45689.6646 | 0.0018259 | 1.1178e-05 | 7 | 1143 | Planned | Planned
3103 |  | 38427 | BAIR K09 - K09 CARTER HOLT | Auckland | BAIR K03 | 2025-02-02 | 45690.191 | 2025-02-02 | 45690.259 | 0.045406 | 0.001032 | 646 | 28424 | Unplanned | Defective equipment
3104 |  | 38427 | BAIR K09 - K09 CARTER HOLT | Auckland | BAIR K09 | 2025-02-02 | 45690.191 | 2025-02-02 | 45690.259 | 0.0010959 | 1.1184e-05 | 7 | 686 | Unplanned | Defective equipment
3105 |  | 38430 | PAPA K05 - K05 EAST ST | Auckland | PAPA K05 | 2025-02-02 | 45690.3139 | 2025-02-02 | 45690.6194 | 0.16267 | 0.0013786 | 863 | 101830 | Unplanned | Third party interference
3106 |  | 38431 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2025-02-02 | 45690.3889 | 2025-02-02 | 45690.459 | 0.0080672 | 7.9873e-05 | 50 | 5050 | Unplanned | Defective equipment
3107 |  | 38432 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-02-02 | 45690.2882 | 2025-02-02 | 45690.3778 | 0.0014425 | 1.1181e-05 | 7 | 903 | Unplanned | Cause unknown
3108 |  | 38433 | FORR K03 - K03 MANUTARA AVENUE | Northern | FORR K03 | 2025-02-02 | 45690.4569 | 2025-02-02 | 45690.6417 | 0.20698 | 0.0011693 | 732 | 129567 | Unplanned | Third party interference
3109 |  | 38433 | FORR K03 - K03 MANUTARA AVENUE | Northern | SUNS K02 | 2025-02-02 | 45690.4569 | 2025-02-02 | 45690.6417 | 0.08203 | 0.0016406 | 1027 | 51350 | Unplanned | Third party interference
3110 |  | 38434 | WAIA K04 - K04 CAPRICORN PLACE | Northern | WAIA K04 | 2025-02-02 | 45690.6722 | 2025-02-02 | 45690.8632 | 0.20614 | 0.0018914 | 1184 | 129040 | Unplanned | Defective equipment
3111 |  | 38435 | SUNS K02 - K02 SYCAMORE DRIVE | Northern | SUNS K02 | 2025-02-02 | 45690.7542 | 2025-02-02 | 45690.7806 | 0.0041278 | 0.00010863 | 68 | 2584 | Unplanned | Defective equipment
3112 |  | 38436 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2025-02-02 | 45690.941 | 2025-02-03 | 45691.1417 | 0.045705 | 0.00015815 | 99 | 28611 | Unplanned | Defective equipment
3113 |  | 38437 | PAPA K06 - K06 13 PORCHESTER RD | Auckland | PAPA K06 | 2025-02-02 | 45690.9187 | 2025-02-03 | 45691.2153 | 0.083937 | 0.00029713 | 186 | 52544 | Planned | Planned
3114 |  | 38438 | AVON K02 - K02 ST JUDE ST.(PENSIONER FLATS) | Auckland | AVON K02 | 2025-02-02 | 45690.9792 | 2025-02-03 | 45691.1514 | 0.2587 | 0.0010431 | 653 | 161944 | Planned | Planned
3115 |  | 38440 | RBEA K10 - K10 SHADON PL | Northern | RBEA K10 | 2025-02-03 | 45691.375 | 2025-02-03 | 45691.7146 | 0.045307 | 9.2653e-05 | 58 | 28362 | Planned | Planned
3116 |  | 38441 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-02-03 | 45691.375 | 2025-02-03 | 45691.6285 | 0.0011661 | 3.195e-06 | 2 | 730 | Planned | Planned
3117 |  | 38442 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2025-02-03 | 45691.3958 | 2025-02-03 | 45691.55 | 0.049294 | 0.00022205 | 139 | 30858 | Planned | Planned
3118 |  | 38443 | PONS K20 - K20 CLARENCE ST | Auckland | PONS K20 | 2025-02-03 | 45691.7542 | 2025-02-03 | 45691.7792 | 0.074416 | 0.0020671 | 1294 | 46584 | Unplanned | Wildlife
3119 |  | 38444 | AVON K11 - K11 TIVERTON RD. | Auckland | AVON K11 | 2025-02-03 | 45691.9583 | 2025-02-04 | 45692.034 | 0.0022636 | 2.0767e-05 | 13 | 1417 | Planned | Planned
3120 |  | 38445 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2025-02-04 | 45692.1042 | 2025-02-04 | 45692.1854 | 0.027662 | 0.00023642 | 148 | 17316 | Planned | Planned
3121 |  | 38446 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-02-03 | 45691.8187 | 2025-02-03 | 45691.8444 | 0.00011821 | 3.195e-06 | 2 | 74 | Unplanned | Defective equipment
3122 |  | 38447 | WAIA K04 - K04 CAPRICORN PLACE | Northern | WAIA K04 | 2025-02-03 | 45691.9028 | 2025-02-03 | 45691.9549 | 0.055592 | 0.00074122 | 464 | 34800 | Unplanned | Defective equipment
3123 |  | 38448 | HOWI K06 - K06 BLEAKHOUSE RD | Auckland | HOWI K06 | 2025-02-04 | 45692.3333 | 2025-02-04 | 45692.5417 | 0.033067 | 0.00011022 | 69 | 20700 | Planned | Planned
3124 |  | 38449 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-02-04 | 45692.3549 | 2025-02-04 | 45692.7278 | 0.03946 | 7.3481e-05 | 46 | 24702 | Planned | Planned
3125 |  | 38450 | BMON K01 - K01 ACHILLES CRESCENT | Northern | BMON K01 | 2025-02-04 | 45692.5208 | 2025-02-04 | 45692.6139 | 0.055655 | 0.00041534 | 260 | 34840 | Unplanned | Defective equipment
3126 |  | 38452 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-02-04 | 45692.4056 | 2025-02-04 | 45692.5139 | 0.016946 | 0.00010863 | 68 | 10608 | Unplanned | Cause unknown
3127 |  | 38454 | LIVE K29 - K29 MOUNT STREET | Auckland | LIVE K29 | 2025-02-04 | 45692.9694 | 2025-02-05 | 45693.0465 | 0.0024825 | 2.2364e-05 | 14 | 1554 | Planned | Planned
3128 |  | 38455 | LIVE K24 - K24 AIREDALE ST TELEPHONE EX | Auckland | LIVE K24 | 2025-02-05 | 45693.084 | 2025-02-05 | 45693.1639 | 0.023331 | 0.00020288 | 127 | 14605 | Planned | Planned
3129 |  | 38456 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-02-04 | 45692.8333 | 2025-02-05 | 45693.1715 | 0.045122 | 9.2652e-05 | 58 | 28246 | Planned | Planned
3130 |  | 38457 | HBUR K03 - K03 MAHARA AVE + LS | Northern | HBUR K03 | 2025-02-04 | 45692.9271 | 2025-02-05 | 45693.0687 | 0.03324 | 0.00016294 | 102 | 20808 | Planned | Planned
3131 |  | 38458 | WAIA K05 - K05 CARLISE ROAD | Northern | WAIA K05 | 2025-02-05 | 45693.1806 | 2025-02-05 | 45693.1944 | 0.0015336 | 7.6678e-05 | 48 | 960 | Unplanned | Defective equipment
3132 |  | 38459 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-02-05 | 45693.3576 | 2025-02-05 | 45693.7014 | 0.0047445 | 9.584e-06 | 6 | 2970 | Planned | Planned
3133 |  | 38460 | BMON K09 - K09 BAYSWATER | Northern | BMON K09 | 2025-02-05 | 45693.3549 | 2025-02-05 | 45693.8083 | 0.19989 | 0.00032109 | 201 | 125127 | Planned | Planned
3134 |  | 38461 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2025-02-05 | 45693.3806 | 2025-02-05 | 45693.7188 | 0.0015559 | 3.195e-06 | 2 | 974 | Planned | Planned
3135 |  | 38462 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-02-05 | 45693.3965 | 2025-02-05 | 45693.4986 | 0.0011741 | 7.987e-06 | 5 | 735 | Planned | Planned
3136 |  | 38463 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-02-05 | 45693.3944 | 2025-02-05 | 45693.4049 | 4.7924e-05 | 3.195e-06 | 2 | 30 | Unplanned | Other Cause | Outage caused by Tap Operation
3137 |  | 38465 | MANU K07 - K07 HALVER RD | Auckland | MANU K07 | 2025-02-05 | 45693.875 | 2025-02-05 | 45693.9049 | 0.0031598 | 7.3483e-05 | 46 | 1978 | Planned | Planned
3138 |  | 38466 | LIVE K04 - K04 AUT BUSINESS SCHOOL | Auckland | LIVE K04 | 2025-02-05 | 45693.9792 | 2025-02-06 | 45694.0486 | 0.00079873 | 7.986e-06 | 5 | 500 | Planned | Planned
3139 |  | 38467 | NEWM K30 - K30 BP CROWHURST ST | Auckland | NEWM K30 | 2025-02-06 | 45694.0868 | 2025-02-06 | 45694.1653 | 0.016066 | 0.00014217 | 89 | 10057 | Planned | Planned
3140 |  | 38468 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2025-02-06 | 45694.1618 | 2025-02-06 | 45694.2611 | 0.0071023 | 0.0003738 | 234 | 4446 | Unplanned | Defective equipment
3141 |  | 38469 | WSWA K05 - K05 RICHARDSON RD O/H LINE EAST VIA LS | Auckland | WSWA K05 | 2025-02-06 | 45694.2285 | 2025-02-06 | 45694.5354 | 0.15007 | 0.0010847 | 407 | 93942 | Unplanned | Third party interference
3142 |  | 38471 | HBUR K03 - K03 MAHARA AVE + LS | Northern | HBUR K03 | 2025-02-06 | 45694.5319 | 2025-02-06 | 45694.75 | 0.058961 | 0.00096327 | 603 | 36909 | Unplanned | Defective equipment
3143 |  | 38473 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2025-02-06 | 45694.8757 | 2025-02-07 | 45695.0215 | 0.058036 | 0.00027636 | 173 | 36330 | Unplanned | Third party interference
3144 |  | 38475 | ROSE K01 - K01 GLUCINA SMELTERS | Auckland | ROSE K01 | 2025-02-07 | 45695.3354 | 2025-02-07 | 45695.6424 | 0.0021182 | 4.792e-06 | 3 | 1326 | Planned | Planned
3145 |  | 38477 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-02-07 | 45695.4924 | 2025-02-07 | 45695.6174 | 0.023698 | 0.00063738 | 399 | 14835 | Unplanned | Third party interference
3146 |  | 38478 | MKAU K09 - K09 CAVENDISH CENTRE | Auckland | MKAU K09 | 2025-02-07 | 45695.5958 | 2025-02-07 | 45695.7917 | 0.0045048 | 7.9872e-05 | 50 | 2820 | Unplanned | Defective equipment
3147 |  | 38480 | VICT K20 - K20 MID CITY TOWERS | Auckland | VICT K20 | 2025-02-07 | 45695.7861 | 2025-02-07 | 45695.9688 | 0.00042013 | 1.597e-06 | 1 | 263 | Unplanned | Defective equipment
3148 |  | 38481 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2025-02-07 | 45695.7931 | 2025-02-07 | 45695.8431 | 0.00057509 | 7.987e-06 | 5 | 360 | Unplanned | Cause unknown
3149 |  | 38482 | GINN K02 - K02 PADDINGTON ST | Auckland | GINN K02 | 2025-02-08 | 45696.0799 | 2025-02-08 | 45696.109 | 0.017578 | 0.00041853 | 262 | 11004 | Unplanned | Defective equipment
3150 |  | 38482 | GINN K02 - K02 PADDINGTON ST | Auckland | SHEL K06 | 2025-02-08 | 45696.0799 | 2025-02-08 | 45696.109 | 0.028313 | 0.00067413 | 422 | 17724 | Unplanned | Defective equipment
3151 |  | 38483 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-02-08 | 45696.1389 | 2025-02-08 | 45696.2951 | 0.12399 | 0.0011454 | 717 | 77616 | Unplanned | Defective equipment
3152 |  | 38484 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2025-02-08 | 45696.766 | 2025-02-08 | 45696.8493 | 0.0001917 | 1.597e-06 | 1 | 120 | Unplanned | Defective equipment
3153 |  | 38486 | HVAL K02 - K02 CORBAN AVENUE | Northern | HVAL K02 | 2025-02-09 | 45697.5382 | 2025-02-09 | 45697.6354 | 0.00044729 | 3.195e-06 | 2 | 280 | Unplanned | Defective equipment
3154 |  | 38487 | SJOH K06 - K06 60 COLLEGE RD | Auckland | SJOH K06 | 2025-02-09 | 45697.7396 | 2025-02-09 | 45697.834 | 0.11118 | 0.0013275 | 831 | 69599 | Unplanned | Third party interference
3155 |  | 38488 | CHEV K09 - K09 PREMIER AVE | Auckland | CHEV K09 | 2025-02-09 | 45697.9257 | 2025-02-10 | 45698.1285 | 0.0013994 | 4.792e-06 | 3 | 876 | Planned | Planned
3156 |  | 38489 | MANU K04 - K04 CENTRE WEYMOUTH RD VIA LS | Auckland | MANU K04 | 2025-02-09 | 45697.9792 | 2025-02-10 | 45698.1764 | 0.22366 | 0.00078755 | 493 | 140012 | Planned | Planned
3157 |  | 38490 | HBUR K03 - K03 MAHARA AVE + LS | Northern | HBUR K03 | 2025-02-09 | 45697.9549 | 2025-02-10 | 45698.0104 | 0.0053435 | 8.6262e-05 | 54 | 3345 | Planned | Planned
3158 |  | 38492 | DRIV K07 - K07 THE DRIVE | Auckland | DRIV K07 | 2025-02-10 | 45698.9583 | 2025-02-11 | 45699.0576 | 0.02627 | 0.00018371 | 115 | 16445 | Planned | Planned
3159 |  | 38493 | WSWA K03 - K03 MARSHALL LAING ST | Auckland | WSWA K03 | 2025-02-11 | 45699.1042 | 2025-02-11 | 45699.2063 | 0.1153 | 0.00078435 | 491 | 72177 | Planned | Planned
3160 |  | 38494 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2025-02-11 | 45699.1861 | 2025-02-11 | 45699.3333 | 0.027757 | 0.00013898 | 87 | 17376 | Unplanned | Cause unknown
3161 |  | 38495 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-02-11 | 45699.2785 | 2025-02-11 | 45699.3611 | 0.0003802 | 3.195e-06 | 2 | 238 | Unplanned | Cause unknown
3162 |  | 38496 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2025-02-11 | 45699.3368 | 2025-02-11 | 45699.3611 | 0.00067093 | 1.917e-05 | 12 | 420 | Unplanned | Defective equipment
3163 |  | 38498 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-02-11 | 45699.375 | 2025-02-11 | 45699.6701 | 0.0047524 | 1.1182e-05 | 7 | 2975 | Planned | Planned
3164 |  | 38499 | LAIN K09 - K09 MACKIES REST | Northern | LAIN K09 | 2025-02-11 | 45699.2493 | 2025-02-11 | 45699.3854 | 0.0025048 | 1.278e-05 | 8 | 1568 | Unplanned | Wildlife
3165 |  | 38500 | RANU K05 - K05 ARMADA DRIVE | Northern | RANU K05 | 2025-02-11 | 45699.375 | 2025-02-11 | 45699.5979 | 0.0035895 | 1.1182e-05 | 7 | 2247 | Planned | Planned
3166 |  | 38501 | SJOH K06 - K06 60 COLLEGE RD | Auckland | SJOH K06 | 2025-02-11 | 45699.375 | 2025-02-11 | 45699.5 | 0.025879 | 0.00014377 | 90 | 16200 | Unplanned | Cause unknown
3167 |  | 38503 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2025-02-11 | 45699.7632 | 2025-02-11 | 45699.9271 | 0.001508 | 6.39e-06 | 4 | 944 | Unplanned | Vegetation
3168 |  | 38504 | HBUR K08 - K08 COLONIAL ROAD | Northern | HBUR K08 | 2025-02-11 | 45699.9285 | 2025-02-12 | 45700.1549 | 0.00096167 | 0.00014856 | 93 | 602 | Unplanned | Third party interference
3169 |  | 38505 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2025-02-11 | 45699.9292 | 2025-02-11 | 45699.984 | 0.0071934 | 9.1051e-05 | 57 | 4503 | Unplanned | Defective equipment
3170 |  | 38506 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-02-11 | 45699.9715 | 2025-02-12 | 45700.1222 | 0.072563 | 0.0013594 | 851 | 45424 | Unplanned | Vegetation
3171 |  | 38507 | ROCK K13 - K13 GREENPARK RD | Auckland | ROCK K13 | 2025-02-11 | 45699.9799 | 2025-02-12 | 45700.1458 | 0.032834 | 0.00013738 | 86 | 20554 | Planned | Planned
3172 |  | 38508 | SIMP K08 - K08 SEIBEL ROAD | Northern | HVAL K13 | 2025-02-12 | 45700.1326 | 2025-02-12 | 45700.1972 | 0.011342 | 0.0028355 | 1775 | 7100 | Unplanned | Cause unknown
3173 |  | 38508 | SIMP K08 - K08 SEIBEL ROAD | Northern | SIMP K08 | 2025-02-12 | 45700.1326 | 2025-02-12 | 45700.1972 | 0.095386 | 0.001885 | 1180 | 59711 | Unplanned | Cause unknown
3174 |  | 38511 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-02-12 | 45700.3333 | 2025-02-12 | 45700.6868 | 0.023104 | 4.9514e-05 | 31 | 14463 | Planned | Planned
3175 |  | 38513 | MANL K01 - K01 ARMY BAY | Northern | MANL K01 | 2025-02-12 | 45700.3958 | 2025-02-12 | 45700.5146 | 0.028956 | 0.00016933 | 106 | 18126 | Planned | Planned
3176 |  | 38514 | MKAU K09 - K09 CAVENDISH CENTRE | Auckland | MKAU K09 | 2025-02-12 | 45700.9583 | 2025-02-13 | 45701.0451 | 0.00059905 | 4.792e-06 | 3 | 375 | Planned | Planned
3177 |  | 38515 | HILL K07 - K07 173 HILLSBOROUGH RD | Auckland | HILL K07 | 2025-02-12 | 45700.9583 | 2025-02-13 | 45701.2264 | 0.43501 | 0.0011358 | 711 | 272313 | Planned | Planned
3178 |  | 38515 | HILL K07 - K07 173 HILLSBOROUGH RD | Auckland | ONEH K11 | 2025-02-12 | 45700.9583 | 2025-02-13 | 45701.2264 | 0.1038 | 0.00027317 | 171 | 64980 | Planned | Planned
3179 |  | 38517 | GREE K13 - K13 COOKES WIRE ROPES | Auckland | GREE K13 | 2025-02-12 | 45700.7611 | 2025-02-12 | 45700.9118 | 0.0006933 | 3.195e-06 | 2 | 434 | Unplanned | Cause unknown
3180 |  | 38518 | AVON K02 - K02 ST JUDE ST.(PENSIONER FLATS) | Auckland | AVON K02 | 2025-02-13 | 45701.0208 | 2025-02-13 | 45701.1153 | 0.014773 | 0.00010863 | 68 | 9248 | Planned | Planned
3181 |  | 38519 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-02-13 | 45701.3354 | 2025-02-13 | 45701.7403 | 0.07502 | 0.00027797 | 126 | 46962 | Planned | Planned
3182 |  | 38520 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-02-13 | 45701.2319 | 2025-02-13 | 45701.3569 | 0.0077637 | 4.3131e-05 | 27 | 4860 | Unplanned | Cause unknown
3183 |  | 38522 | SABU K04 - K04 GLENDENE | Northern | KEEL K06 | 2025-02-13 | 45701.5222 | 2025-02-13 | 45701.5778 | 0.0066215 | 0.0013243 | 829 | 4145 | Unplanned | Defective equipment
3184 |  | 38522 | SABU K04 - K04 GLENDENE | Northern | SABU K04 | 2025-02-13 | 45701.5222 | 2025-02-13 | 45701.5778 | 0.10052 | 0.0061806 | 2236 | 62927 | Unplanned | Defective equipment
3185 |  | 38523 | PAKU K04 - K04 REEVES RD | Auckland | PAKU K04 | 2024-04-23 | 45405.375 | 2024-04-23 | 45405.6875 | 0.096327 | 0.00021406 | 134 | 60300 | Planned | Planned
3186 |  | 38524 | SHEL K04 - K04 YATTENDON RD VIA LS | Auckland | SHEL K04 | 2025-02-13 | 45701.9174 | 2025-02-14 | 45702.1382 | 0.056895 | 0.00017892 | 112 | 35616 | Planned | Planned
3187 |  | 38525 | LIVE K03 - K03 385 OTAGO UNIVERSITY | Auckland | LIVE K03 | 2025-02-13 | 45701.9583 | 2025-02-14 | 45702.0271 | 0.015815 | 0.00015975 | 100 | 9900 | Planned | Planned
3188 |  | 38526 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2025-02-13 | 45701.9792 | 2025-02-14 | 45702.0778 | 0.045141 | 0.00031789 | 199 | 28258 | Planned | Planned
3189 |  | 38527 | NEWT K19 - K19 JOHN ANDREW | Auckland | NEWT K19 | 2025-02-14 | 45702.0833 | 2025-02-14 | 45702.1625 | 0.0056454 | 4.9521e-05 | 31 | 3534 | Planned | Planned
3190 |  | 38528 | NLYN K04 - K04 RATA ST | Northern | NLYN K04 | 2025-02-14 | 45702.375 | 2025-02-14 | 45702.7299 | 0.034285 | 6.7093e-05 | 42 | 21462 | Planned | Planned
3191 |  | 38531 | ORAK K05 - K05 GODDEN CRES | Auckland | ORAK K05 | 2025-02-14 | 45702.9375 | 2025-02-15 | 45703.2667 | 0.097678 | 0.00020607 | 129 | 61146 | Planned | Planned
3192 |  | 38532 | ONEH K12 - K12 - SELWYN ST SOUTH + LS | Auckland | ONEH K12 | 2025-02-15 | 45703.0903 | 2025-02-15 | 45703.2972 | 0.18207 | 0.0014377 | 900 | 113976 | Unplanned | Defective equipment
3193 |  | 38534 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-02-15 | 45703.3771 | 2025-02-15 | 45703.6347 | 0.039523 | 0.00057512 | 243 | 24741 | Unplanned | Defective equipment
3194 |  | 38535 | NSBT83 - ORATIA H01 - LAINGHOLM P290 (83) | Northern | ORAT K02 | 2025-02-15 | 45703.8778 | 2025-02-15 | 45703.9556 | 0.001738 | 0.00010224 | 64 | 1088 | Unplanned | Vegetation
3195 |  | 38536 | SJOH K03 - K03 96 NGAHUE DR | Auckland | SJOH K03 | 2025-02-15 | 45703.3264 | 2025-02-16 | 45704.0611 | 0.0010336 | 7.987e-06 | 5 | 647 | Unplanned | Third party interference
3196 |  | 38537 | SABU K05 - K05 GLENVIEW RD | Northern | SABU K05 | 2025-02-16 | 45704.3542 | 2025-02-16 | 45704.6694 | 0.015955 | 3.5144e-05 | 22 | 9988 | Planned | Planned
3197 |  | 38538 | WSWA K17 - K17 RICHARDSON RD O/H LINE WEST | Auckland | WSWA K17 | 2025-02-16 | 45704.266 | 2025-02-16 | 45704.3889 | 0.036192 | 0.00020447 | 128 | 22656 | Unplanned | Cause unknown
3198 |  | 38539 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2025-02-16 | 45704.3111 | 2025-02-16 | 45704.4167 | 0.0019425 | 1.2779e-05 | 8 | 1216 | Unplanned | Wildlife
3199 |  | 38540 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2025-02-16 | 45704.4576 | 2025-02-16 | 45704.534 | 0.014409 | 0.00013099 | 82 | 9020 | Unplanned | Defective equipment
3200 |  | 38541 | SNEL K08 - K08 ALGIES BAY | Northern | SNEL K08 | 2025-02-16 | 45704.4903 | 2025-02-16 | 45704.4931 | 0.00036422 | 9.1055e-05 | 57 | 228 | Unplanned | Other Cause | Outage caused by Tap Operation
3201 |  | 38542 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2025-02-16 | 45704.6861 | 2025-02-16 | 45704.7604 | 0.0013674 | 1.2779e-05 | 8 | 856 | Unplanned | Wildlife
3202 |  | 38543 | GHIT K02 - K02 ORWELL RD | Northern | GHIT K02 | 2025-02-16 | 45704.8861 | 2025-02-16 | 45704.9201 | 0.043678 | 0.00089138 | 558 | 27342 | Unplanned | Third party interference
3203 |  | 38544 | TPAP K12 - K12 282-286 CHURCH ST | Auckland | TPAP K12 | 2025-02-16 | 45704.9583 | 2025-02-17 | 45705.0437 | 0.0043227 | 3.5144e-05 | 22 | 2706 | Planned | Planned
3204 |  | 38545 | WSWA K09 - K09 ELLIS AVENUE | Auckland | WSWA K09 | 2025-02-17 | 45705.0076 | 2025-02-17 | 45705.075 | 0.033005 | 0.00034026 | 213 | 20661 | Planned | Planned
3205 |  | 38546 | SYLV K15 - K15 25 CARBINE RD SW STN | Auckland | SYLV K15 | 2025-02-17 | 45705.0882 | 2025-02-17 | 45705.1632 | 0.0039681 | 3.6742e-05 | 23 | 2484 | Planned | Planned
3206 |  | 38547 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2025-02-17 | 45705.4201 | 2025-02-17 | 45705.5243 | 0.003115 | 2.0767e-05 | 13 | 1950 | Planned | Planned
3207 |  | 38548 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2025-02-17 | 45705.7889 | 2025-02-18 | 45706.1042 | 0.022788 | 0.00080193 | 502 | 14265 | Unplanned | Defective equipment
3208 |  | 38549 | SYLV K15 - K15 25 CARBINE RD SW STN | Auckland | SYLV K15 | 2025-02-17 | 45705.9792 | 2025-02-18 | 45706.1299 | 0.005893 | 2.7156e-05 | 17 | 3689 | Planned | Planned
3209 |  | 38550 | CHEV K09 - K09 PREMIER AVE | Auckland | CHEV K09 | 2025-02-18 | 45706.0021 | 2025-02-18 | 45706.1354 | 0.00092014 | 4.792e-06 | 3 | 576 | Planned | Planned
3210 |  | 38551 | NEWM K04 - K04 MAHURU ST | Auckland | NEWM K04 | 2025-02-18 | 45706.0535 | 2025-02-18 | 45706.2937 | 0.1368 | 0.0015671 | 790 | 85634 | Unplanned | Vegetation
3211 |  | 38552 | OREW K04 - K04 WATERLOO | Northern | OREW K04 | 2025-02-18 | 45706.3542 | 2025-02-18 | 45706.6493 | 0.0033946 | 7.987e-06 | 5 | 2125 | Planned | Planned
3212 |  | 38553 | BMON K01 - K01 ACHILLES CRESCENT | Northern | BMON K01 | 2025-02-18 | 45706.3757 | 2025-02-18 | 45706.6104 | 0.038336 | 0.00011342 | 71 | 23998 | Planned | Planned
3213 |  | 38554 | HILL K09 - K09 3 MELROSE RD | Auckland | HILL K09 | 2025-02-18 | 45706.3812 | 2025-02-18 | 45706.4486 | 0.022767 | 0.00026838 | 168 | 14252 | Planned | Planned
3214 |  | 38555 | CLEN K09 - K09 WEYMOUTH SOUTH | Auckland | CLEN K09 | 2025-02-18 | 45706.3965 | 2025-02-18 | 45706.484 | 0.013083 | 0.00010383 | 65 | 8190 | Planned | Planned
3215 |  | 38556 | KEEL K12 - K12 STURGES RD | Northern | KEEL K12 | 2025-02-18 | 45706.3958 | 2025-02-18 | 45706.5437 | 0.040491 | 0.0001901 | 119 | 25347 | Planned | Planned
3216 |  | 38557 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-02-18 | 45706.4465 | 2025-02-18 | 45706.4681 | 0.00044569 | 1.4377e-05 | 9 | 279 | Unplanned | Defective equipment
3217 |  | 38558 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2025-02-18 | 45706.5229 | 2025-02-18 | 45706.5944 | 0.03044 | 0.00029553 | 185 | 19055 | Unplanned | Vegetation
3218 |  | 38559 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-02-18 | 45706.5354 | 2025-02-18 | 45706.6625 | 0.00029234 | 1.597e-06 | 1 | 183 | Unplanned | Defective equipment
3219 |  | 38560 | WIRI K18 - K18 ASH RD | Auckland | WIRI K18 | 2025-02-18 | 45706.684 | 2025-02-18 | 45706.7729 | 0.013254 | 0.00012301 | 77 | 8297 | Unplanned | Defective equipment
3220 |  | 38561 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-02-18 | 45706.6875 | 2025-02-18 | 45706.7021 | 0.00010064 | 4.792e-06 | 3 | 63 | Unplanned | Defective equipment
3221 |  | 38562 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2025-02-18 | 45706.6632 | 2025-02-18 | 45706.7257 | 0.00028754 | 3.195e-06 | 2 | 180 | Unplanned | Cause unknown
3222 |  | 38563 | TPAP K12 - K12 282-286 CHURCH ST | Auckland | TPAP K12 | 2025-02-18 | 45706.9583 | 2025-02-19 | 45707.0417 | 0.0001917 | 1.597e-06 | 1 | 120 | Planned | Planned
3223 |  | 38564 | REMU K12 - K12 PEACH PARADE | Auckland | REMU K12 | 2025-02-19 | 45707.0833 | 2025-02-19 | 45707.1667 | 0.011885 | 9.9042e-05 | 62 | 7440 | Planned | Planned
3224 |  | 38565 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2025-02-19 | 45707.2083 | 2025-02-19 | 45707.7049 | 0.061961 | 0.00058307 | 365 | 38787 | Planned | Planned
3225 |  | 38566 | SHOW K14 - K14 WHITFORD RD VIA LS | Auckland | SHOW K14 | 2025-02-19 | 45707.2882 | 2025-02-19 | 45707.3611 | 0.0020128 | 1.917e-05 | 12 | 1260 | Unplanned | Cause unknown
3226 |  | 38567 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2025-02-19 | 45707.3806 | 2025-02-19 | 45707.7583 | 0.036609 | 0.00042812 | 143 | 22917 | Planned | Planned
3227 |  | 38568 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-02-19 | 45707.3958 | 2025-02-19 | 45707.6181 | 0.0040895 | 1.2779e-05 | 8 | 2560 | Planned | Planned
3228 |  | 38569 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2025-02-19 | 45707.7389 | 2025-02-19 | 45707.7444 | 0.0019297 | 0.00024122 | 151 | 1208 | Unplanned | Defective equipment
3229 |  | 38570 | COAT K12 - K12 MAHOENUI VALLEY | Northern | COAT K12 | 2025-02-19 | 45707.7417 | 2025-02-19 | 45707.8493 | 0.00099043 | 6.39e-06 | 4 | 620 | Unplanned | Vegetation
3230 |  | 38571 | TATA K08 - K08 HEREFORD STREET | Northern | TATA K08 | 2025-02-19 | 45707.9167 | 2025-02-20 | 45708.0271 | 0.059173 | 0.00040895 | 256 | 37042 | Planned | Planned
3231 |  | 38572 | BRIC K09 - K09 VERONICA ST | Northern | BRIC K09 | 2025-02-19 | 45707.9167 | 2025-02-20 | 45708.1243 | 0.0028658 | 9.585e-06 | 6 | 1794 | Planned | Planned
3232 |  | 38573 | REMU K18 - K18 HAAST ST | Auckland | REMU K18 | 2025-02-19 | 45707.9583 | 2025-02-20 | 45708.0403 | 0.043921 | 0.00037221 | 233 | 27494 | Planned | Planned
3233 |  | 38574 | REMU K18 - K18 HAAST ST | Auckland | REMU K18 | 2025-02-20 | 45708.0833 | 2025-02-20 | 45708.1646 | 0.016261 | 0.00013898 | 87 | 10179 | Planned | Planned
3234 |  | 38575 | HPOI K06 - K06 WISELEY RD | Northern | HPOI K06 | 2025-02-20 | 45708.334 | 2025-02-20 | 45708.691 | 0.07347 | 0.00014697 | 92 | 45992 | Planned | Planned
3235 |  | 38576 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-02-20 | 45708.334 | 2025-02-20 | 45708.7396 | 0.041048 | 7.0287e-05 | 44 | 25696 | Planned | Planned
3236 |  | 38577 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2025-02-20 | 45708.3542 | 2025-02-20 | 45708.7375 | 0.276 | 0.0005 | 313 | 172776 | Planned | Planned
3237 |  | 38578 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-02-20 | 45708.375 | 2025-02-20 | 45708.7083 | 0.0099602 | 2.0767e-05 | 13 | 6235 | Planned | Planned
3238 |  | 38579 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-02-20 | 45708.375 | 2025-02-20 | 45708.4458 | 0.017923 | 0.00017571 | 110 | 11220 | Planned | Planned
3239 |  | 38580 | WEST K11 - K11 WESTFIELD BASEMENT | Auckland | WEST K11 | 2025-02-18 | 45706.6917 | 2025-02-20 | 45708.4736 | 0.04509 | 1.7572e-05 | 11 | 28226 | Unplanned | Defective equipment
3240 |  | 38583 | HVAL K03 - K03 BRUCE McLAREN | Northern | HVAL K03 | 2025-02-20 | 45708.8542 | 2025-02-20 | 45708.8715 | 0.0015575 | 6.2301e-05 | 39 | 975 | Unplanned | Wildlife
3241 |  | 38584 | SABU K02 - K02 HEPBURN RD | Northern | SABU K02 | 2025-02-20 | 45708.9167 | 2025-02-21 | 45709.0222 | 0.00097125 | 6.39e-06 | 4 | 608 | Planned | Planned
3242 |  | 38585 | NEWM K10 - K10 SMITH EQUITY | Auckland | NEWM K10 | 2025-02-20 | 45708.9583 | 2025-02-21 | 45709.0368 | 0.011553 | 0.00010224 | 64 | 7232 | Planned | Planned
3243 |  | 38586 | ETAM K20 - K20 13 HIGHBROOK DR | Auckland | ETAM K20 | 2025-02-21 | 45709.0833 | 2025-02-21 | 45709.1583 | 0.0015527 | 1.4377e-05 | 9 | 972 | Planned | Planned
3244 |  | 38588 | CLEN K09 - K09 WEYMOUTH SOUTH | Auckland | CLEN K09 | 2025-02-21 | 45709.375 | 2025-02-21 | 45709.65 | 0.033029 | 8.4665e-05 | 53 | 20676 | Planned | Planned
3245 |  | 38590 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2025-02-21 | 45709.3688 | 2025-02-21 | 45709.4514 | 0.028286 | 0.00029071 | 162 | 17707 | Unplanned | Cause unknown
3246 |  | 38592 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-02-21 | 45709.4792 | 2025-02-21 | 45709.8701 | 0.056531 | 0.00010065 | 63 | 35388 | Planned | Planned
3247 |  | 38593 | MNAB K06 - K06 PENROSE RYTHMATIC | Auckland | MNAB K06 | 2025-02-21 | 45709.9236 | 2025-02-22 | 45710.1917 | 0.0012332 | 3.195e-06 | 2 | 772 | Planned | Planned
3248 |  | 38595 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2025-02-22 | 45710.4167 | 2025-02-22 | 45710.5486 | 0.00030352 | 1.597e-06 | 1 | 190 | Planned | Planned
3249 |  | 38597 | BROW K03 - K03 JOHN DOWNS DRIVE | Northern | BROW K03 | 2025-02-22 | 45710.7069 | 2025-02-22 | 45710.7486 | 0.042844 | 0.00071406 | 447 | 26820 | Unplanned | Vegetation
3250 |  | 38598 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2025-02-23 | 45711.1785 | 2025-02-23 | 45711.2528 | 0.032574 | 0.0014329 | 531 | 20391 | Unplanned | Wildlife
3251 |  | 38600 | SNEL K11 - K11 GRANGE | Northern | SNEL K11 | 2025-02-23 | 45711.8924 | 2025-02-23 | 45711.9313 | 0.00071566 | 1.2779e-05 | 8 | 448 | Unplanned | Cause unknown
3252 |  | 38601 | HOWI K13 - K13 MALVINA PL | Auckland | HOWI K13 | 2025-02-24 | 45712.1042 | 2025-02-24 | 45712.1292 | 0.0024154 | 6.7093e-05 | 42 | 1512 | Planned | Planned
3253 |  | 38602 | MCEN K12 - K12 ROBERTSON ROAD SOUTH | Auckland | MCEN K12 | 2025-02-24 | 45712.3965 | 2025-02-24 | 45712.5035 | 0.0019681 | 1.278e-05 | 8 | 1232 | Planned | Planned
3254 |  | 38603 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-02-24 | 45712.3819 | 2025-02-24 | 45712.6389 | 0.0023371 | 6.39e-06 | 4 | 1463 | Planned | Planned
3255 |  | 38605 | SAND K14 - K14 2 WAITE AVE | Auckland | SAND K14 | 2025-02-24 | 45712.6993 | 2025-02-24 | 45712.8146 | 0.034082 | 0.00076519 | 479 | 21335 | Unplanned | Cause unknown
3256 |  | 38606 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-02-24 | 45712.5236 | 2025-02-24 | 45712.9431 | 0.0048243 | 7.987e-06 | 5 | 3020 | Unplanned | Human error
3257 |  | 38607 | SABU K08 - K08 GREAT NORTH RD | Northern | SABU K08 | 2025-02-24 | 45712.8208 | 2025-02-24 | 45712.891 | 0.027428 | 0.00027157 | 170 | 17170 | Unplanned | Defective equipment
3258 |  | 38608 | NEWT K18 - K18 SYMONDS ST 226 | Auckland | NEWT K18 | 2025-02-25 | 45713 | 2025-02-25 | 45713.1597 | 0.0084506 | 3.6742e-05 | 23 | 5290 | Planned | Planned
3259 |  | 38609 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-02-25 | 45713.2507 | 2025-02-25 | 45713.8313 | 0.030591 | 0.00047764 | 297 | 19150 | Planned | Planned
3260 |  | 38610 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-02-25 | 45713.3333 | 2025-02-25 | 45713.6562 | 0.01857 | 3.9936e-05 | 25 | 11625 | Planned | Planned
3261 |  | 38611 | SIMP K10 - K10 CANDIA ROAD + LS | Northern | SIMP K10 | 2025-02-25 | 45713.3368 | 2025-02-25 | 45713.3403 | 0.00027157 | 5.4314e-05 | 34 | 170 | Unplanned | Wildlife
3262 |  | 38612 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-02-25 | 45713.616 | 2025-02-25 | 45713.7903 | 0.027666 | 0.00011022 | 69 | 17319 | Unplanned | Defective equipment
3263 |  | 38613 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2025-02-25 | 45713.3347 | 2025-02-25 | 45713.7528 | 0.301 | 0.0005 | 313 | 188426 | Planned | Planned
3264 |  | 38615 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2025-02-26 | 45714.3542 | 2025-02-26 | 45714.7278 | 0.12118 | 0.00022524 | 141 | 75858 | Planned | Planned
3265 |  | 38616 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-02-26 | 45714.3333 | 2025-02-27 | 45715.6667 | 0.012205 | 2.5562e-05 | 8 | 7640 | Planned | Planned
3266 |  | 38617 | SABU K07 - K07 AWAROA RD | Northern | SABU K07 | 2025-02-26 | 45714.3812 | 2025-02-26 | 45714.4833 | 0.0096279 | 6.5496e-05 | 41 | 6027 | Planned | Planned
3267 |  | 38618 | SHEL K04 - K04 YATTENDON RD VIA LS | Auckland | SHEL K04 | 2025-02-26 | 45714.4007 | 2025-02-26 | 45714.5632 | 0.041866 | 0.00017892 | 112 | 26208 | Planned | Planned
3268 |  | 38620 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2025-02-26 | 45714.3958 | 2025-02-26 | 45714.709 | 0.017291 | 3.8338e-05 | 24 | 10824 | Planned | Planned
3269 |  | 38621 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2025-02-26 | 45714.6076 | 2025-02-26 | 45714.6354 | 0.0026837 | 6.7091e-05 | 42 | 1680 | Unplanned | Defective equipment
3270 |  | 38622 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-02-26 | 45714.6521 | 2025-02-26 | 45714.7028 | 0.00011661 | 1.597e-06 | 1 | 73 | Unplanned | Wildlife
3271 |  | 38623 | HCRE K06 - K06 TAHAROTO ROAD | Northern | HCRE K06 | 2025-02-26 | 45714.9167 | 2025-02-27 | 45715.0681 | 0.16681 | 0.00076518 | 479 | 104422 | Planned | Planned
3272 |  | 38624 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-02-27 | 45715.2347 | 2025-02-27 | 45715.3597 | 0.00057509 | 3.195e-06 | 2 | 360 | Unplanned | Cause unknown
3273 |  | 38625 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K06 | 2025-02-27 | 45715.334 | 2025-02-27 | 45715.8243 | 0.0053116 | 7.987e-06 | 5 | 3325 | Planned | Planned
3274 |  | 38625 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-02-27 | 45715.334 | 2025-02-27 | 45715.8243 | 0.14196 | 0.00020126 | 126 | 88869 | Planned | Planned
3275 |  | 38626 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2025-02-27 | 45715.3542 | 2025-02-27 | 45715.6792 | 0.10541 | 0.00022524 | 141 | 65988 | Planned | Planned
3276 |  | 38627 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2025-02-27 | 45715.3757 | 2025-02-27 | 45715.75 | 0.094102 | 0.00021565 | 122 | 58907 | Planned | Planned
3277 |  | 38628 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-02-27 | 45715.5986 | 2025-02-27 | 45715.6292 | 0.016939 | 0.00038497 | 241 | 10604 | Unplanned | Cause unknown
3278 |  | 38629 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-02-27 | 45715.7924 | 2025-02-27 | 45715.8299 | 0.025448 | 0.00047125 | 295 | 15930 | Planned | Planned
3279 |  | 38630 | WAIR K10 - K10 NILE ROAD | Northern | WAIR K10 | 2025-02-27 | 45715.875 | 2025-02-27 | 45715.9958 | 0.00027796 | 1.597e-06 | 1 | 174 | Planned | Planned
3280 |  | 38631 | ASBT273B - BROOKBY H02 - MARAETAI H06 | Auckland | FBSH K13 | 2025-02-27 | 45715.9868 | 2025-02-28 | 45716.9257 | 0.079164 | 0.00021726 | 136 | 49556 | Unplanned | Third party interference
3281 |  | 38632 | ROSE K02 - K02 ROSEBANK RD SOUTH | Auckland | ROSE K02 | 2025-02-28 | 45716.0424 | 2025-02-28 | 45716.1986 | 0.0014377 | 6.39e-06 | 4 | 900 | Planned | Planned
3282 |  | 38634 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-02-28 | 45716.375 | 2025-02-28 | 45716.625 | 0.0046007 | 1.278e-05 | 8 | 2880 | Planned | Planned
3283 |  | 38635 | WAIR K07 - K07 BECROFT | Northern | WAIR K07 | 2025-02-28 | 45716.334 | 2025-02-28 | 45716.6979 | 0.19209 | 0.00038658 | 242 | 120247 | Planned | Planned
3284 |  | 38637 | SNEL K10 - K10 KAWAU ISL | Northern | SNEL K10 | 2025-02-28 | 45716.3542 | 2025-02-28 | 45716.6813 | 0.234 | 0.0004968 | 311 | 146481 | Planned | Planned
3285 |  | 38638 | WAIH K03 - K03 WHAKARITE RD | Auckland | WAIH K03 | 2025-02-28 | 45716.2875 | 2025-02-28 | 45716.359 | 0.015138 | 0.00014697 | 92 | 9476 | Unplanned | Wildlife
3286 |  | 38640 | ONEH K08 - K08 - TAWA RD | Auckland | ONEH K08 | 2025-02-28 | 45716.3958 | 2025-02-28 | 45716.5729 | 0.20082 | 0.00078755 | 493 | 125715 | Planned | Planned
3287 |  | 38641 | MWEL K06 - K06 WAIPUNA RD 58 | Auckland | MWEL K06 | 2025-02-28 | 45716.4167 | 2025-02-28 | 45716.5729 | 0.03774 | 0.00016773 | 105 | 23625 | Planned | Planned
3288 |  | 38642 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-02-28 | 45716.2215 | 2025-02-28 | 45716.4062 | 0.0029745 | 1.1182e-05 | 7 | 1862 | Unplanned | Vegetation
3289 |  | 38645 | HOBV K10 - K10 OREIL AVENUE | Northern | HOBV K10 | 2025-02-28 | 45716.8354 | 2025-03-01 | 45717.4292 | 0.061755 | 0.00032908 | 206 | 38658 | Planned | Planned
3290 |  | 38646 | PAPA K10 - K10 17 PORCHESTER RD | Auckland | PAPA K10 | 2025-02-28 | 45716.8493 | 2025-03-01 | 45717.1 | 0.40329 | 0.002532 | 1585 | 252458 | Unplanned | Third party interference
3291 |  | 38647 | NCOT K02 - K02 HARBOUR BRIDGE + LS | Northern | NCOT K02 | 2025-02-28 | 45716.7514 | 2025-02-28 | 45716.8632 | 0.00025719 | 1.597e-06 | 1 | 161 | Unplanned | Cause unknown
3292 |  | 38649 | BAIR K02 - K02 KERWYN AVE | Auckland | BAIR K02 | 2025-03-01 | 45717.3854 | 2025-03-01 | 45717.4854 | 0.00023003 | 1.597e-06 | 1 | 144 | Planned | Planned
3293 |  | 38651 | PAPA K10 - K10 17 PORCHESTER RD | Auckland | PAPA K10 | 2025-03-01 | 45717.6722 | 2025-03-01 | 45717.7528 | 0.081582 | 0.00070608 | 442 | 51070 | Unplanned | Third party interference
3294 |  | 38652 | TAKA K17 - K17 CLEVEDON | Auckland | TAKA K17 | 2025-03-01 | 45717.8625 | 2025-03-02 | 45718.6146 | 0.039869 | 0.00029233 | 162 | 24958 | Unplanned | Third party interference
3295 |  | 38653 | ORAT K03 - K03 SCENIC DRIVE | Northern | ORAT K03 | 2025-03-01 | 45717.9549 | 2025-03-02 | 45718 | 0.0016614 | 2.5559e-05 | 16 | 1040 | Unplanned | Defective equipment
3296 |  | 38655 | RANU K04 - K04 GLEN ROAD | Northern | RANU K04 | 2025-03-02 | 45718.5833 | 2025-03-02 | 45718.5972 | 3.1949e-05 | 1.597e-06 | 1 | 20 | Unplanned | Vegetation
3297 |  | 38656 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-03-02 | 45718.5472 | 2025-03-02 | 45718.6181 | 0.00032588 | 3.195e-06 | 2 | 204 | Unplanned | Wildlife
3298 |  | 38657 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-02 | 45718.7264 | 2025-03-02 | 45718.8229 | 0.0015543 | 1.1182e-05 | 7 | 973 | Unplanned | Cause unknown
3299 |  | 38658 | ONEH K12 - K12 - SELWYN ST SOUTH + LS | Auckland | ONEH K12 | 2025-03-02 | 45718.9583 | 2025-03-03 | 45719.2056 | 0.062493 | 0.00019169 | 120 | 39120 | Planned | Planned
3300 |  | 38660 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-03 | 45719.3472 | 2025-03-03 | 45719.4479 | 0.0014138 | 1.7572e-05 | 11 | 885 | Planned | Planned
3301 |  | 38663 | TPAP K08 - K08 CHURCH ST WEST VIA LS | Auckland | TPAP K08 | 2025-03-03 | 45719.9792 | 2025-03-04 | 45720.3306 | 0.13822 | 0.00027317 | 171 | 86526 | Unplanned | Third party interference
3302 |  | 38665 | NLYN K01 - K01 ARAWA ST | Northern | NLYN K01 | 2025-03-04 | 45720.4715 | 2025-03-04 | 45720.4993 | 0.034377 | 0.00085943 | 538 | 21520 | Unplanned | Other Cause | Outage on Non-Vector asset
3303 |  | 38666 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-03-04 | 45720.775 | 2025-03-04 | 45720.8174 | 9.7445e-05 | 1.597e-06 | 1 | 61 | Unplanned | Cause unknown
3304 |  | 38668 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-04 | 45720.9819 | 2025-03-05 | 45721.4632 | 0.28782 | 0.002144 | 1027 | 180174 | Unplanned | Defective equipment
3305 |  | 38668 | SWAN K07 - K07 BETHELLS | Northern | SWAN K08 | 2025-03-04 | 45720.9819 | 2025-03-05 | 45721.4632 | 0.0024281 | 0.00063897 | 80 | 1520 | Unplanned | Defective equipment
3306 |  | 38669 | VICT K22 - K22 QUEEN STREET (MERCURY) | Auckland | VICT K22 | 2025-03-05 | 45721.0104 | 2025-03-05 | 45721.1562 | 0.00067093 | 3.194e-06 | 2 | 420 | Planned | Planned
3307 |  | 38670 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2025-03-05 | 45721.0417 | 2025-03-05 | 45721.1125 | 0.12856 | 0.0012604 | 789 | 80478 | Planned | Planned
3308 |  | 38671 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2025-03-05 | 45721.2931 | 2025-03-05 | 45721.5757 | 0.053314 | 0.00013099 | 82 | 33374 | Unplanned | Defective equipment
3309 |  | 38671 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K09 | 2025-03-05 | 45721.2931 | 2025-03-05 | 45721.5757 | 0.0026007 | 6.389e-06 | 4 | 1628 | Unplanned | Defective equipment
3310 |  | 38672 | RIVE K03 - K03 BRIGHAMS CREEK | Northern | RIVE K03 | 2025-03-05 | 45721.3576 | 2025-03-05 | 45721.6736 | 0.0014537 | 3.195e-06 | 2 | 910 | Planned | Planned
3311 |  | 38673 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2025-03-05 | 45721.3576 | 2025-03-05 | 45721.7194 | 0.11069 | 0.00021246 | 133 | 69293 | Planned | Planned
3312 |  | 38674 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-03-05 | 45721.3333 | 2025-03-05 | 45721.6528 | 0.098467 | 0.00021406 | 134 | 61640 | Planned | Planned
3313 |  | 38675 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-03-05 | 45721.375 | 2025-03-05 | 45721.6604 | 0.051211 | 0.0001246 | 78 | 32058 | Planned | Planned
3314 |  | 38676 | ATKI K11 - K11 PLEASANT RD | Northern | ATKI K11 | 2025-03-05 | 45721.3958 | 2025-03-05 | 45721.6042 | 0.014377 | 4.7924e-05 | 30 | 9000 | Planned | Planned
3315 |  | 38677 | HANS K06 - K06 SUPREME STEEL | Auckland | HANS K06 | 2025-03-05 | 45721.3819 | 2025-03-05 | 45721.5868 | 0.0009425 | 3.195e-06 | 2 | 590 | Planned | Planned
3316 |  | 38678 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-03-05 | 45721.6701 | 2025-03-05 | 45721.8854 | 0.020898 | 0.00016614 | 104 | 13082 | Unplanned | Defective equipment
3317 |  | 38679 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-05 | 45721.816 | 2025-03-05 | 45721.8194 | 7.987e-06 | 1.597e-06 | 1 | 5 | Unplanned | Other Cause | Outage caused by Tap Operation
3318 |  | 38680 | SHEL K05 - K05 RIDDELL RD WEST | Auckland | SHEL K05 | 2025-03-05 | 45721.9799 | 2025-03-06 | 45722.0771 | 0.035783 | 0.00025559 | 160 | 22400 | Planned | Planned
3319 |  | 38681 | HANS K27 - K27 NIKAU ROAD | Auckland | HANS K27 | 2025-03-05 | 45721.9792 | 2025-03-06 | 45722.2063 | 0.035521 | 0.00010863 | 68 | 22236 | Planned | Planned
3320 |  | 38682 | REMU K18 - K18 HAAST ST | Auckland | REMU K18 | 2025-03-06 | 45722.1056 | 2025-03-06 | 45722.2201 | 0.015024 | 9.1055e-05 | 57 | 9405 | Planned | Planned
3321 |  | 38683 | HOBV K10 - K10 OREIL AVENUE | Northern | HOBV K10 | 2025-03-06 | 45722.1875 | 2025-03-06 | 45722.2194 | 0.010883 | 0.00032428 | 203 | 6813 | Planned | Planned
3322 |  | 38685 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2025-03-06 | 45722.309 | 2025-03-06 | 45722.3847 | 0.017989 | 0.00063577 | 398 | 11261 | Unplanned | Cause unknown
3323 |  | 38686 | WARK K05 - K05 SATELLITE | Northern | WARK K04 | 2025-03-06 | 45722.3542 | 2025-03-06 | 45722.7097 | 0.0097765 | 1.9167e-05 | 12 | 6120 | Planned | Planned
3324 |  | 38686 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-03-06 | 45722.3542 | 2025-03-06 | 45722.7097 | 0.037623 | 7.3476e-05 | 46 | 23552 | Planned | Planned
3325 |  | 38687 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2025-03-06 | 45722.3333 | 2025-03-06 | 45722.7083 | 0.0051758 | 9.585e-06 | 6 | 3240 | Planned | Planned
3326 |  | 38688 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-06 | 45722.3819 | 2025-03-06 | 45722.7604 | 0.019928 | 3.6742e-05 | 23 | 12475 | Planned | Planned
3327 |  | 38689 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-03-06 | 45722.3757 | 2025-03-06 | 45722.6042 | 0.063593 | 0.00019329 | 121 | 39809 | Planned | Planned
3328 |  | 38690 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K06 | 2025-03-06 | 45722.5632 | 2025-03-06 | 45722.6069 | 0.0023483 | 0.000254 | 82 | 1470 | Unplanned | Human error
3329 |  | 38690 | WAIM K06 - K06 FOSTER RD | Northern | WAIM K09 | 2025-03-06 | 45722.5632 | 2025-03-06 | 45722.6069 | 0.00040256 | 6.387e-06 | 4 | 252 | Unplanned | Human error
3330 |  | 38691 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2025-03-06 | 45722.6389 | 2025-03-06 | 45722.8083 | 0.020269 | 8.3067e-05 | 52 | 12688 | Unplanned | Vegetation
3331 |  | 38691 | MANU K12 - K12 ALFRISTON RD | Auckland | TAKA K12 | 2025-03-06 | 45722.6389 | 2025-03-06 | 45722.8083 | 0.0019968 | 3.9936e-05 | 25 | 1250 | Unplanned | Vegetation
3332 |  | 38692 | NEWM K04 - K04 MAHURU ST | Auckland | NEWM K04 | 2025-03-06 | 45722.7847 | 2025-03-06 | 45722.8125 | 0.0011502 | 2.8754e-05 | 18 | 720 | Unplanned | Third party interference
3333 |  | 38693 | MANL K10 - K10 MATAI ROAD | Northern | MANL K10 | 2025-03-07 | 45723.0764 | 2025-03-07 | 45723.4764 | 0.034259 | 0.00019808 | 62 | 21446 | Unplanned | Defective equipment
3334 |  | 38694 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-07 | 45723.2111 | 2025-03-07 | 45723.3257 | 0.0013179 | 7.987e-06 | 5 | 825 | Unplanned | Wildlife
3335 |  | 38695 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-07 | 45723.3542 | 2025-03-07 | 45723.7174 | 0.071851 | 0.00013738 | 86 | 44978 | Planned | Planned
3336 |  | 38696 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-03-07 | 45723.3819 | 2025-03-07 | 45723.5285 | 0.022246 | 0.00010543 | 66 | 13926 | Planned | Planned
3337 |  | 38697 | MKAU K18 - K18 MANUKAU CITY HEALTH CENTRE | Auckland | MKAU K18 | 2025-03-07 | 45723.3097 | 2025-03-08 | 45724.3333 | 0.0047093 | 3.195e-06 | 2 | 2948 | Unplanned | Cause unknown
3338 |  | 38698 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-07 | 45723.4313 | 2025-03-07 | 45723.6417 | 0.0026214 | 2.8752e-05 | 18 | 1641 | Planned | Planned
3339 |  | 38701 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-03-07 | 45723.6806 | 2025-03-07 | 45723.7326 | 0.0020368 | 2.7155e-05 | 17 | 1275 | Unplanned | Defective equipment
3340 |  | 38704 | SHEL K04 - K04 YATTENDON RD VIA LS | Auckland | SHEL K04 | 2025-03-07 | 45723.9167 | 2025-03-08 | 45724.1965 | 0.040558 | 0.00010064 | 63 | 25389 | Planned | Planned
3341 |  | 38705 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2025-03-08 | 45724.1056 | 2025-03-08 | 45724.1722 | 0.00046007 | 4.792e-06 | 3 | 288 | Unplanned | Cause unknown
3342 |  | 38706 | BIRK K12 - K12 STANLEY ROAD | Northern | BIRK K12 | 2025-03-08 | 45724.3611 | 2025-03-08 | 45724.7174 | 0.062282 | 0.00012141 | 76 | 38988 | Planned | Planned
3343 |  | 38707 | HVAL K04 - K04 GARELJA RD | Northern | HVAL K04 | 2025-03-08 | 45724.4313 | 2025-03-09 | 45725.7694 | 0.041202 | 0.00019489 | 75 | 25792 | Unplanned | Defective equipment
3344 |  | 38708 | BIRK K02 - K02 DOMAIN ROAD | Northern | BIRK K02 | 2025-03-08 | 45724.4167 | 2025-03-08 | 45724.5569 | 0.01323 | 6.5496e-05 | 41 | 8282 | Planned | Planned
3345 |  | 38710 | MARA K05 - K05 REWA RD | Auckland | MARA K05 | 2025-03-09 | 45725.0007 | 2025-03-09 | 45725.0708 | 0.00080672 | 7.987e-06 | 5 | 505 | Unplanned | Wildlife
3346 |  | 38711 | HAUR - Hauraki | Northern | HAUR K01 | 2025-03-09 | 45725.2576 | 2025-03-09 | 45725.7139 | 0.13009 | 0.0029234 | 915 | 81435 | Unplanned | Defective equipment
3347 |  | 38711 | HAUR - Hauraki | Northern | HAUR K02 | 2025-03-09 | 45725.2576 | 2025-03-09 | 45725.7139 | 0.066422 | 0.0014761 | 462 | 41580 | Unplanned | Defective equipment
3348 |  | 38711 | HAUR - Hauraki | Northern | HAUR K04 | 2025-03-09 | 45725.2576 | 2025-03-09 | 45725.7139 | 0.13754 | 0.0019649 | 1230 | 86100 | Unplanned | Defective equipment
3349 |  | 38711 | HAUR - Hauraki | Northern | HAUR K05 | 2025-03-09 | 45725.2576 | 2025-03-09 | 45725.7139 | 0.094745 | 0.0010527 | 659 | 59310 | Unplanned | Defective equipment
3350 |  | 38712 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-03-09 | 45725.8764 | 2025-03-10 | 45726.2396 | 0.072771 | 0.00017572 | 98 | 45554 | Planned | Planned
3351 |  | 38713 | ORAK K10 - K10 DUDLEY RD | Auckland | ORAK K10 | 2025-03-09 | 45725.9792 | 2025-03-10 | 45726.1528 | 0.053116 | 0.00021246 | 133 | 33250 | Planned | Planned
3352 |  | 38714 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2025-03-10 | 45726.0417 | 2025-03-10 | 45726.1556 | 0.2067 | 0.0012604 | 789 | 129396 | Planned | Planned
3353 |  | 38716 | MLEO K02 - K02 ROBERTS ROAD | Northern | MLEO K02 | 2025-03-10 | 45726.3729 | 2025-03-10 | 45726.7521 | 0.10379 | 0.0001901 | 119 | 64974 | Planned | Planned
3354 |  | 38717 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2025-03-10 | 45726.3764 | 2025-03-10 | 45726.3861 | 0.0020064 | 0.00017412 | 109 | 1256 | Planned | Planned
3355 |  | 38718 | WOOD K05 - K05 FAIRDENE AVE | Northern | WOOD K05 | 2025-03-10 | 45726.375 | 2025-03-10 | 45726.7326 | 0.066638 | 0.00012939 | 81 | 41715 | Planned | Planned
3356 |  | 38719 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-03-10 | 45726.5021 | 2025-03-10 | 45726.5188 | 3.8339e-05 | 1.597e-06 | 1 | 24 | Planned | Planned
3357 |  | 38720 | WIRI K13 - K13 117 KERRS RD | Auckland | WIRI K13 | 2025-03-10 | 45726.4236 | 2025-03-10 | 45726.4542 | 0.0027956 | 7.9883e-05 | 50 | 1750 | Unplanned | Cause unknown
3358 |  | 38721 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-03-10 | 45726.4174 | 2025-03-10 | 45726.4285 | 2.5559e-05 | 1.597e-06 | 1 | 16 | Planned | Planned
3359 |  | 38722 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-03-10 | 45726.4375 | 2025-03-10 | 45726.4444 | 4.7924e-05 | 4.792e-06 | 3 | 30 | Planned | Planned
3360 |  | 38723 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2025-03-10 | 45726.5625 | 2025-03-10 | 45726.5729 | 0 | 0 | 0 | 0 | Planned | Planned
3361 |  | 38724 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-03-10 | 45726.5847 | 2025-03-10 | 45726.5979 | 0.00012141 | 6.39e-06 | 4 | 76 | Planned | Planned
3362 |  | 38726 | BMON K01 - K01 ACHILLES CRESCENT | Northern | BMON K01 | 2025-03-10 | 45726.7083 | 2025-03-10 | 45726.7194 | 0.00010224 | 6.39e-06 | 4 | 64 | Unplanned | Other Cause | Outage caused by Tap Operation
3363 |  | 38727 | CHEV K05 - K05 PT CHEVALIER RD 22 | Auckland | CHEV K05 | 2025-03-10 | 45726.9382 | 2025-03-11 | 45727.2132 | 0.079074 | 0.00019968 | 125 | 49500 | Planned | Planned
3364 |  | 38728 | FREE K64 - K64 WELLINGTON ST (131) (NEW) | Auckland | FREE K64 | 2025-03-10 | 45726.9583 | 2025-03-11 | 45727.034 | 0.0397 | 0.00036422 | 228 | 24852 | Planned | Planned
3365 |  | 38729 | HOBS K24 - K24 63 ALBERT ST | Auckland | HOBS K24 | 2025-03-11 | 45727.0729 | 2025-03-11 | 45727.1868 | 0.00026198 | 1.597e-06 | 1 | 164 | Planned | Planned
3366 |  | 38730 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-03-10 | 45726.875 | 2025-03-11 | 45727.2431 | 0.073406 | 0.00017572 | 98 | 45952 | Planned | Planned
3367 |  | 38731 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-03-10 | 45726.8611 | 2025-03-10 | 45726.9479 | 0.00019968 | 1.597e-06 | 1 | 125 | Unplanned | Wildlife
3368 |  | 38732 | WOOD K05 - K05 FAIRDENE AVE | Northern | WOOD K05 | 2025-03-11 | 45727.1875 | 2025-03-13 | 45729.2472 | 0.094801 | 0.0013259 | 415 | 59345 | Planned | Planned
3369 |  | 38733 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-03-11 | 45727.3549 | 2025-03-11 | 45727.6528 | 0.0027412 | 6.39e-06 | 4 | 1716 | Planned | Planned
3370 |  | 38734 | ECOA K04 - K04 KNIGHTS ROAD | Northern | ECOA K04 | 2025-03-11 | 45727.3958 | 2025-03-11 | 45727.6042 | 0.1246 | 0.00041534 | 260 | 78000 | Planned | Planned
3371 |  | 38735 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2025-03-11 | 45727.375 | 2025-03-11 | 45727.3924 | 0.0013978 | 5.5911e-05 | 35 | 875 | Planned | Planned
3372 |  | 38736 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-03-11 | 45727.375 | 2025-03-11 | 45727.7917 | 0.07136 | 0.00011981 | 75 | 44671 | Planned | Planned
3373 |  | 38737 | ATKI K06 - K06 OTITORI BAY | Northern | ATKI K06 | 2025-03-11 | 45727.4375 | 2025-03-11 | 45727.4479 | 0.00083867 | 5.5911e-05 | 35 | 525 | Planned | Planned
3374 |  | 38738 | FORR K03 - K03 MANUTARA AVENUE | Northern | FORR K03 | 2025-03-11 | 45727.4187 | 2025-03-11 | 45727.4639 | 0.074838 | 0.001647 | 730 | 46848 | Unplanned | Cause unknown
3375 |  | 38739 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2025-03-11 | 45727.375 | 2025-03-11 | 45727.3896 | 0.00040256 | 1.917e-05 | 12 | 252 | Planned | Planned
3376 |  | 38740 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-03-11 | 45727.4889 | 2025-03-11 | 45727.4903 | 0.00065816 | 0.00032907 | 206 | 412 | Unplanned | Vegetation
3377 |  | 38741 | HELE K10 - K10 KAUKAPAKAPA | Northern | HELE K10 | 2025-03-11 | 45727.5243 | 2025-03-11 | 45727.5361 | 2.7157e-05 | 1.597e-06 | 1 | 17 | Planned | Planned
3378 |  | 38742 | ATKI K03 - K03 GODLEY RD | Northern | ATKI K03 | 2025-03-11 | 45727.5208 | 2025-03-11 | 45727.5264 | 0.00024281 | 3.0352e-05 | 19 | 152 | Planned | Planned
3379 |  | 38743 | HELE K10 - K10 KAUKAPAKAPA | Northern | HELE K10 | 2025-03-11 | 45727.616 | 2025-03-11 | 45727.6194 | 7.987e-06 | 1.597e-06 | 1 | 5 | Planned | Planned
3380 |  | 38744 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2025-03-11 | 45727.6042 | 2025-03-11 | 45727.6146 | 0.00016773 | 1.1182e-05 | 7 | 105 | Planned | Planned
3381 |  | 38745 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | MKAU K19 | 2025-03-11 | 45727.9583 | 2025-03-12 | 45728.0451 | 0.04393 | 0.00035144 | 220 | 27500 | Planned | Planned
3382 |  | 38746 | MKAU K07 - K07 TE IRIRANGI DRIVE | Auckland | MKAU K07 | 2025-03-12 | 45728.1035 | 2025-03-12 | 45728.1757 | 0.028243 | 0.00027157 | 170 | 17680 | Planned | Planned
3383 |  | 38747 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-03-12 | 45728.0444 | 2025-03-12 | 45728.3382 | 0.1117 | 0.0028132 | 973 | 69923 | Unplanned | Wildlife
3384 |  | 38748 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-03-12 | 45728.3764 | 2025-03-12 | 45728.6472 | 0.029281 | 7.5078e-05 | 47 | 18330 | Planned | Planned
3385 |  | 38749 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-03-12 | 45728.375 | 2025-03-12 | 45728.5736 | 0.00045687 | 1.597e-06 | 1 | 286 | Planned | Planned
3386 |  | 38750 | RBEA K10 - K10 SHADON PL | Northern | RBEA K10 | 2025-03-12 | 45728.375 | 2025-03-12 | 45728.4132 | 0.0033387 | 6.0703e-05 | 38 | 2090 | Planned | Planned
3387 |  | 38751 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-03-12 | 45728.375 | 2025-03-12 | 45728.6354 | 0.01258 | 3.3544e-05 | 21 | 7875 | Planned | Planned
3388 |  | 38752 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-03-12 | 45728.3556 | 2025-03-12 | 45728.6972 | 0.0070735 | 1.4377e-05 | 9 | 4428 | Planned | Planned
3389 |  | 38755 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-03-12 | 45728.216 | 2025-03-12 | 45728.3646 | 0.00068371 | 3.195e-06 | 2 | 428 | Unplanned | Cause unknown
3390 |  | 38757 | BROW K09 - K09 STAPLEFORD CRESCENT | Northern | BROW K09 | 2025-03-12 | 45728.375 | 2025-03-12 | 45728.709 | 0.082216 | 0.00017093 | 107 | 51467 | Planned | Planned
3391 |  | 38758 | HOWI K06 - K06 BLEAKHOUSE RD | Auckland | HOWI K06 | 2025-03-12 | 45728.4167 | 2025-03-12 | 45728.5444 | 0.1164 | 0.00063259 | 396 | 72864 | Planned | Planned
3392 |  | 38759 | MANL K10 - K10 MATAI ROAD | Northern | MANL K10 | 2025-03-12 | 45728.4174 | 2025-03-12 | 45728.6285 | 0.026182 | 0.00019808 | 62 | 16390 | Planned | Planned
3393 |  | 38760 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-03-12 | 45728.375 | 2025-03-12 | 45728.6632 | 0.01127 | 2.7156e-05 | 17 | 7055 | Planned | Planned
3394 |  | 38762 | MLEO K05 - K05 CARHAVEN | Northern | MLEO K05 | 2025-03-12 | 45728.875 | 2025-03-13 | 45729.0271 | 0.0062972 | 2.8754e-05 | 18 | 3942 | Planned | Planned
3395 |  | 38763 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-03-12 | 45728.9583 | 2025-03-13 | 45729.1035 | 0.049079 | 0.00023483 | 147 | 30723 | Planned | Planned
3396 |  | 38765 | PONS K08 - K08 VERMONT ST | Auckland | PONS K08 | 2025-03-12 | 45728.9583 | 2025-03-13 | 45729.2007 | 0.34287 | 0.00098244 | 615 | 214635 | Planned | Planned
3397 |  | 38766 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-03-13 | 45729.2306 | 2025-03-13 | 45729.4333 | 0.00093292 | 3.195e-06 | 2 | 584 | Unplanned | Wildlife
3398 |  | 38767 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-13 | 45729.3542 | 2025-03-13 | 45729.6375 | 0.00065176 | 1.597e-06 | 1 | 408 | Planned | Planned
3399 |  | 38768 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2025-03-13 | 45729.3542 | 2025-03-13 | 45729.7021 | 0.10164 | 0.00020288 | 127 | 63627 | Planned | Planned
3400 |  | 38769 | SUNS K01 - K01 LANDSBERG WAY | Northern | SUNS K01 | 2025-03-13 | 45729.3611 | 2025-03-13 | 45729.7465 | 0.00088659 | 1.597e-06 | 1 | 555 | Planned | Planned
3401 |  | 38770 | HVAL K13 - K13 PIHA | Northern | HVAL K13 | 2025-03-13 | 45729.3569 | 2025-03-13 | 45729.6694 | 0.0064697 | 1.4377e-05 | 9 | 4050 | Planned | Planned
3402 |  | 38771 | KKAP K03 - K03 KAHIKATEA FLAT RD | Northern | KKAP K03 | 2025-03-13 | 45729.375 | 2025-03-13 | 45729.6833 | 0.028371 | 6.3895e-05 | 40 | 17760 | Planned | Planned
3403 |  | 38772 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-03-13 | 45729.375 | 2025-03-13 | 45729.6153 | 0.00055272 | 1.597e-06 | 1 | 346 | Planned | Planned
3404 |  | 38773 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-03-13 | 45729.375 | 2025-03-13 | 45729.6507 | 0.03932 | 9.9042e-05 | 62 | 24614 | Planned | Planned
3405 |  | 38775 | NGAT K07 - K07 PATUONE AVE | Northern | NGAT K07 | 2025-03-13 | 45729.6083 | 2025-03-13 | 45729.6215 | 0.0030016 | 0.00017412 | 109 | 1879 | Planned | Planned
3406 |  | 38776 | LAIN K07 - K07 VICTORY RD | Northern | LAIN K07 | 2025-03-13 | 45729.5486 | 2025-03-13 | 45729.6687 | 0.053614 | 0.00030991 | 194 | 33562 | Unplanned | Defective equipment
3407 |  | 38778 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2025-03-13 | 45729.9375 | 2025-03-14 | 45730.041 | 0.00095209 | 6.39e-06 | 4 | 596 | Planned | Planned
3408 |  | 38779 | HANS K27 - K27 NIKAU ROAD | Auckland | HANS K27 | 2025-03-13 | 45729.9799 | 2025-03-14 | 45730.216 | 0.036933 | 0.00010863 | 68 | 23120 | Planned | Planned
3409 |  | 38780 | MKAU K07 - K07 TE IRIRANGI DRIVE | Auckland | MKAU K07 | 2025-03-13 | 45729.9889 | 2025-03-14 | 45730.1521 | 0.11262 | 0.00047924 | 300 | 70500 | Planned | Planned
3410 |  | 38782 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-03-14 | 45730.3333 | 2025-03-14 | 45730.7083 | 0.10438 | 0.00019329 | 121 | 65340 | Planned | Planned
3411 |  | 38783 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2025-03-14 | 45730.3542 | 2025-03-14 | 45730.7174 | 0.0050128 | 9.585e-06 | 6 | 3138 | Planned | Planned
3412 |  | 38784 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2025-03-14 | 45730.3819 | 2025-03-14 | 45730.7049 | 0.0014856 | 3.195e-06 | 2 | 930 | Planned | Planned
3413 |  | 38785 | BRIC K09 - K09 VERONICA ST | Northern | BRIC K09 | 2025-03-14 | 45730.3056 | 2025-03-14 | 45730.5431 | 0.003278 | 9.585e-06 | 6 | 2052 | Unplanned | Defective equipment
3414 |  | 38786 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2025-03-14 | 45730.5153 | 2025-03-14 | 45730.6979 | 0.0012604 | 4.792e-06 | 3 | 789 | Unplanned | Third party interference
3415 |  | 38787 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-03-14 | 45730.8458 | 2025-03-14 | 45730.9174 | 0.00082269 | 7.987e-06 | 5 | 515 | Unplanned | Wildlife
3416 |  | 38788 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2025-03-14 | 45730.9229 | 2025-03-15 | 45731.3326 | 0.24393 | 0.00041534 | 260 | 152701 | Planned | Planned
3417 |  | 38789 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-03-15 | 45731.1694 | 2025-03-15 | 45731.25 | 0.00037061 | 3.195e-06 | 2 | 232 | Unplanned | Cause unknown
3418 |  | 38790 | RIVE K10 - K10 HUAPAI | Northern | RIVE K10 | 2025-03-15 | 45731.3757 | 2025-03-15 | 45731.5792 | 0.008425 | 2.8754e-05 | 18 | 5274 | Planned | Planned
3419 |  | 38791 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2025-03-15 | 45731.3847 | 2025-03-15 | 45731.5257 | 0.067127 | 0.00033067 | 207 | 42021 | Planned | Planned
3420 |  | 38792 | SUNS K08 - K08 TARGET ROAD | Northern | SUNS K08 | 2025-03-15 | 45731.9167 | 2025-03-16 | 45732.2049 | 0.0033147 | 7.987e-06 | 5 | 2075 | Planned | Planned
3421 |  | 38793 | COAT K03 - K03 SCREEN ROAD | Northern | COAT K03 | 2025-03-16 | 45732.4201 | 2025-03-16 | 45732.5507 | 0.063969 | 0.00034025 | 213 | 40044 | Unplanned | Defective equipment
3422 |  | 38795 | MEAS K16 - K16 WILLOWHAVEN HOSPITAL | Auckland | MEAS K16 | 2025-03-16 | 45732.6062 | 2025-03-16 | 45732.6069 | 0.0040623 | 0.0040623 | 2543 | 2543 | Unplanned | Human error
3423 |  | 38796 | MEAS K12 - K12 MASSEY RD | Auckland | MEAS K12 | 2025-03-16 | 45732.9618 | 2025-03-17 | 45733.1979 | 0.016837 | 4.9521e-05 | 31 | 10540 | Planned | Planned
3424 |  | 38797 | SJOH K05 - K05 69 MERTON RD | Auckland | SJOH K05 | 2025-03-16 | 45732.9583 | 2025-03-17 | 45733.0431 | 0.048138 | 0.00039457 | 247 | 30134 | Planned | Planned
3425 |  | 38798 | SJOH K06 - K06 60 COLLEGE RD | Auckland | SJOH K06 | 2025-03-16 | 45732.9792 | 2025-03-17 | 45733.0361 | 0.015719 | 0.0001917 | 120 | 9840 | Planned | Planned
3426 |  | 38799 | ROSE K10 - K10 ROSEBANK RD NORTH | Auckland | ROSE K10 | 2025-03-17 | 45733.2896 | 2025-03-17 | 45733.7639 | 0.0010911 | 1.597e-06 | 1 | 683 | Unplanned | Cause unknown
3427 |  | 38800 | BRIC K03 - K03 CROWN LYNN PL | Northern | BRIC K03 | 2025-03-17 | 45733.3979 | 2025-03-17 | 45733.6007 | 0.0069969 | 2.3962e-05 | 15 | 4380 | Planned | Planned
3428 |  | 38801 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-17 | 45733.4375 | 2025-03-17 | 45733.4757 | 0.00035144 | 6.39e-06 | 4 | 220 | Planned | Planned
3429 |  | 38802 | WGAT K04 - K04 NORTHSIDE DR | Northern | WGAT K04 | 2025-03-17 | 45733.6208 | 2025-03-17 | 45733.7014 | 0.068801 | 0.0015447 | 967 | 43069 | Unplanned | Vegetation
3430 |  | 38803 | MKAU K09 - K09 CAVENDISH CENTRE | Auckland | MKAU K09 | 2025-03-17 | 45733.9583 | 2025-03-18 | 45734.0437 | 0.0017684 | 1.4377e-05 | 9 | 1107 | Planned | Planned
3431 |  | 38804 | MANU K08 - K08 6 GREAT SOUTH RD | Auckland | MANU K08 | 2025-03-18 | 45734.1062 | 2025-03-18 | 45734.1958 | 0.033384 | 0.00025879 | 162 | 20898 | Planned | Planned
3432 |  | 38805 | RIVE K09 - K09 KUMEU | Northern | RIVE K09 | 2025-03-18 | 45734.3333 | 2025-03-18 | 45734.5444 | 0.00097125 | 3.195e-06 | 2 | 608 | Planned | Planned
3433 |  | 38806 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2025-03-18 | 45734.3368 | 2025-03-18 | 45734.6743 | 0.0015527 | 3.195e-06 | 2 | 972 | Planned | Planned
3434 |  | 38807 | BUSH K08 - K08 UNITY DR | Northern | BUSH K08 | 2025-03-18 | 45734.3542 | 2025-03-18 | 45734.5222 | 0.00038658 | 1.597e-06 | 1 | 242 | Planned | Planned
3435 |  | 38808 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-03-18 | 45734.3542 | 2025-03-18 | 45734.5896 | 0.0016246 | 4.792e-06 | 3 | 1017 | Planned | Planned
3436 |  | 38809 | SPUR K02 - K02 REDVALE | Northern | SPUR K02 | 2025-03-18 | 45734.375 | 2025-03-18 | 45734.591 | 0.11278 | 0.00036262 | 227 | 70597 | Planned | Planned
3437 |  | 38810 | KING K02 - K02 KINGSLAND AVE | Auckland | KING K02 | 2025-03-18 | 45734.3681 | 2025-03-18 | 45734.5618 | 0.10807 | 0.0015272 | 956 | 67652 | Unplanned | Wildlife
3438 |  | 38811 | ORAK K13 - K13 35 THATCHER ST | Auckland | ORAK K13 | 2025-03-18 | 45734.3958 | 2025-03-18 | 45734.6819 | 0.088193 | 0.00021406 | 134 | 55208 | Planned | Planned
3439 |  | 38812 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-18 | 45734.3958 | 2025-03-18 | 45734.6007 | 0.051366 | 0.00017412 | 109 | 32155 | Planned | Planned
3440 |  | 38813 | MANL K10 - K10 MATAI ROAD | Northern | MANL K10 | 2025-03-18 | 45734.4437 | 2025-03-18 | 45734.5299 | 0.012281 | 9.9043e-05 | 62 | 7688 | Planned | Planned
3441 |  | 38814 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2025-03-18 | 45734.4632 | 2025-03-18 | 45734.541 | 0.045714 | 0.0011278 | 706 | 28617 | Unplanned | Cause unknown
3442 |  | 38815 | KKAP K02 - K02 KANOHI RD | Northern | KKAP K02 | 2025-03-18 | 45734.4993 | 2025-03-18 | 45734.7653 | 0.065025 | 0.00058622 | 367 | 40705 | Unplanned | Defective equipment
3443 |  | 38816 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K07 | 2025-03-18 | 45734.5285 | 2025-03-18 | 45734.6576 | 0.12604 | 0.001385 | 867 | 78899 | Unplanned | Cause unknown
3444 |  | 38816 | SWAN K08 - K08 O'NEILLS RD | Northern | SWAN K08 | 2025-03-18 | 45734.5285 | 2025-03-18 | 45734.6576 | 0.0016614 | 0.00012779 | 80 | 1040 | Unplanned | Cause unknown
3445 |  | 38817 | MANU K04 - K04 CENTRE WEYMOUTH RD VIA LS | Auckland | MANU K04 | 2025-03-18 | 45734.6604 | 2025-03-18 | 45734.9604 | 0.23187 | 0.00053675 | 336 | 145152 | Unplanned | Third party interference
3446 |  | 38818 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2025-03-18 | 45734.5528 | 2025-03-18 | 45734.7611 | 0.010064 | 3.3545e-05 | 21 | 6300 | Unplanned | Defective equipment
3447 |  | 38819 | MANU K12 - K12 ALFRISTON RD | Auckland | MANU K12 | 2025-03-18 | 45734.9792 | 2025-03-19 | 45735.1493 | 0.053227 | 0.00021725 | 136 | 33320 | Planned | Planned
3448 |  | 38820 | VICT K22 - K22 QUEEN STREET (MERCURY) | Auckland | VICT K22 | 2025-03-19 | 45735.0215 | 2025-03-19 | 45735.1708 | 0.040711 | 0.0001901 | 119 | 25485 | Planned | Planned
3449 |  | 38822 | MARA K04 - K04 WHITFORD VIA LS | Auckland | MARA K04 | 2025-03-19 | 45735.1021 | 2025-03-19 | 45735.5174 | 0.006687 | 1.1182e-05 | 7 | 4186 | Unplanned | Defective equipment
3450 |  | 38824 | COAT K05 - K05 SUNNYSIDE ROAD | Northern | COAT K05 | 2025-03-19 | 45735.3542 | 2025-03-19 | 45735.7153 | 0.039873 | 7.6677e-05 | 48 | 24960 | Planned | Planned
3451 |  | 38825 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-03-19 | 45735.334 | 2025-03-19 | 45735.7035 | 0.024198 | 4.9514e-05 | 31 | 15148 | Planned | Planned
3452 |  | 38826 | PAPA K02 - K02 ONSLOW RD | Auckland | PAPA K02 | 2025-03-19 | 45735.4313 | 2025-03-19 | 45735.5403 | 0.028341 | 0.00018051 | 113 | 17741 | Planned | Planned
3453 |  | 38827 | BAIR K13 - K13 124 GREAT SOUTH RD. | Auckland | BAIR K13 | 2025-03-19 | 45735.5229 | 2025-03-19 | 45735.6875 | 0.062133 | 0.0041758 | 2614 | 38895 | Unplanned | Defective equipment
3454 |  | 38828 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-19 | 45735.6611 | 2025-03-19 | 45735.6986 | 0.00034505 | 6.39e-06 | 4 | 216 | Planned | Planned
3455 |  | 38829 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2025-03-19 | 45735.6757 | 2025-03-19 | 45735.9174 | 0.045106 | 0.00014539 | 91 | 28236 | Unplanned | Vegetation
3456 |  | 38831 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-19 | 45735.6868 | 2025-03-19 | 45735.8035 | 0.041329 | 0.00024599 | 154 | 25872 | Unplanned | Cause unknown
3457 |  | 38832 | SNEL K07 - K07 PARKLANDS + LS | Northern | SNEL K07 | 2025-03-19 | 45735.6875 | 2025-03-19 | 45735.7188 | 0.0017253 | 3.8339e-05 | 24 | 1080 | Unplanned | Defective equipment
3458 |  | 38833 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-03-19 | 45735.725 | 2025-03-19 | 45735.7444 | 0.0031151 | 0.00021564 | 135 | 1950 | Unplanned | Human error
3459 |  | 38834 | SHEL K04 - K04 YATTENDON RD VIA LS | Auckland | SHEL K04 | 2025-03-19 | 45735.9174 | 2025-03-20 | 45736.1674 | 0.03623 | 0.00010064 | 63 | 22680 | Planned | Planned
3460 |  | 38835 | SJOH K10 - K10 82 NORMAN LESSER DR | Auckland | SJOH K10 | 2025-03-19 | 45735.9583 | 2025-03-20 | 45736.0465 | 0.0064921 | 5.1119e-05 | 32 | 4064 | Planned | Planned
3461 |  | 38836 | HOWI K16 - K16 PAKURANGA RD (497) | Auckland | HOWI K16 | 2025-03-20 | 45736.0833 | 2025-03-20 | 45736.166 | 0.010455 | 8.786e-05 | 55 | 6545 | Planned | Planned
3462 |  | 38837 | REMU K12 - K12 PEACH PARADE | Auckland | REMU K12 | 2025-03-20 | 45736.0896 | 2025-03-20 | 45736.1076 | 0.012709 | 0.00048882 | 306 | 7956 | Unplanned | Vegetation
3463 |  | 38838 | HOBV K10 - K10 OREIL AVENUE | Northern | HOBV K10 | 2025-03-19 | 45735.8875 | 2025-03-20 | 45736.0396 | 0.021983 | 0.0006901 | 229 | 13761 | Planned | Planned
3464 |  | 38839 | WGAT K03 - K03 ST CATHERINE | Northern | WGAT K03 | 2025-03-20 | 45736.2451 | 2025-03-20 | 45736.2847 | 0.010289 | 0.00018051 | 113 | 6441 | Unplanned | Defective equipment
3465 |  | 38840 | WAIK K01 - K01 ARIES | Northern | WAIK K01 | 2025-03-20 | 45736.3146 | 2025-03-20 | 45736.3264 | 0.00076039 | 4.4729e-05 | 28 | 476 | Unplanned | Cause unknown
3466 |  | 38841 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2025-03-20 | 45736.3986 | 2025-03-20 | 45736.7889 | 0.076811 | 0.00015016 | 94 | 48083 | Planned | Planned
3467 |  | 38842 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-03-20 | 45736.4625 | 2025-03-20 | 45736.7049 | 0.074707 | 0.00021405 | 134 | 46766 | Planned | Planned
3468 |  | 38843 | RANU K02 - K02 ZITA MARIA | Northern | RANU K02 | 2025-03-20 | 45736.3542 | 2025-03-20 | 45736.7201 | 0.010944 | 2.0767e-05 | 13 | 6851 | Planned | Planned
3469 |  | 38844 | SPUR K07 - K07 PINEVALLEY | Northern | SPUR K07 | 2025-03-20 | 45736.3542 | 2025-03-20 | 45736.6903 | 0.084276 | 0.00017412 | 109 | 52756 | Planned | Planned
3470 |  | 38845 | WAIM K05 - K05 MURIWAI | Northern | WAIM K05 | 2025-03-20 | 45736.375 | 2025-03-20 | 45736.5868 | 0.00048722 | 1.597e-06 | 1 | 305 | Planned | Planned
3471 |  | 38846 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-03-20 | 45736.4278 | 2025-03-20 | 45736.6028 | 0.010869 | 4.3131e-05 | 27 | 6804 | Unplanned | Cause unknown
3472 |  | 38847 | MCEN K13 - K13 MASCOT AVENUE | Auckland | MCEN K13 | 2025-03-20 | 45736.509 | 2025-03-20 | 45736.6375 | 0.050304 | 0.00045847 | 287 | 31490 | Unplanned | Third party interference
3473 |  | 38850 | MEAS K11 - K11 WINTHROP WAY | Auckland | MEAS K11 | 2025-03-20 | 45736.6604 | 2025-03-20 | 45736.9965 | 0.0070113 | 2.0768e-05 | 13 | 4389 | Unplanned | Defective equipment
3474 |  | 38851 | MEAS K12 - K12 MASSEY RD | Auckland | MEAS K12 | 2025-03-20 | 45736.959 | 2025-03-21 | 45737.1924 | 0.016639 | 4.9521e-05 | 31 | 10416 | Planned | Planned
3475 |  | 38852 | MKAU K16 - K16 BAKERFIELD PLACE (VIA LST2) | Auckland | MKAU K16 | 2025-03-20 | 45736.9583 | 2025-03-21 | 45737.0312 | 0.007548 | 7.1886e-05 | 45 | 4725 | Planned | Planned
3476 |  | 38853 | SYLV K02 - K02 MT WELLINGTON HWY VIA RMU | Auckland | SYLV K02 | 2025-03-21 | 45737.025 | 2025-03-21 | 45737.2153 | 0.052524 | 0.0001917 | 120 | 32880 | Planned | Planned
3477 |  | 38854 | MANU K21 - K21 NORTHCREST WAY | Auckland | MANU K21 | 2025-03-21 | 45737.0833 | 2025-03-21 | 45737.1813 | 0.0058563 | 4.1534e-05 | 26 | 3666 | Planned | Planned
3478 |  | 38855 | HANS K08 - K08 MANGERE RD | Auckland | HANS K08 | 2025-03-21 | 45737.0451 | 2025-03-21 | 45737.0514 | 0.0001246 | 1.9172e-05 | 12 | 78 | Planned | Planned
3479 |  | 38856 | LAIN K01 - K01 WOODLANDS + LS | Northern | LAIN K01 | 2025-03-21 | 45737.3542 | 2025-03-21 | 45737.7063 | 0.0032396 | 6.39e-06 | 4 | 2028 | Planned | Planned
3480 |  | 38857 | WARK K13 - K13 KAIPARA FLATS | Northern | WARK K13 | 2025-03-21 | 45737.375 | 2025-03-21 | 45737.6361 | 0.020422 | 5.431e-05 | 34 | 12784 | Planned | Planned
3481 |  | 38858 | GREE K08 - K08 GREENMOUNT DRIVE VIA LS | Auckland | GREE K08 | 2025-03-21 | 45737.3958 | 2025-03-21 | 45737.5333 | 0.020243 | 0.00010224 | 64 | 12672 | Planned | Planned
3482 |  | 38859 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-03-21 | 45737.4493 | 2025-03-21 | 45737.4507 | 3.195e-06 | 1.597e-06 | 1 | 2 | Unplanned | Other Cause | Outage caused by Tap Operation
3483 |  | 38861 | JAME K04 - K04 ELLICE ROAD | Northern | JAME K04 | 2025-03-21 | 45737.6125 | 2025-03-21 | 45737.6535 | 0.0019793 | 3.3547e-05 | 21 | 1239 | Unplanned | Defective equipment
3484 |  | 38862 | NSBT60 - TP WELLSFORD 1092 - WARKWORTH P286 (60) | Northern | WELL K07 | 2025-03-21 | 45737.6389 | 2025-03-22 | 45738.0451 | 0.048754 | 0.0027445 | 1718 | 30520 | Unplanned | Defective equipment
3485 |  | 38862 | NSBT60 - TP WELLSFORD 1092 - WARKWORTH P286 (60) | Northern | WELL K09 | 2025-03-21 | 45737.6389 | 2025-03-22 | 45738.0451 | 0.01842 | 0.0010318 | 646 | 11531 | Unplanned | Defective equipment
3486 |  | 38865 | HELE K05 - K05 SOUTH HEAD | Northern | HELE K05 | 2025-03-21 | 45737.7646 | 2025-03-21 | 45737.8097 | 0.00031151 | 4.792e-06 | 3 | 195 | Unplanned | Wildlife
3487 |  | 38866 | BRIC K10 - K10 ASTLEY AVE | Northern | BRIC K10 | 2025-03-21 | 45737.8264 | 2025-03-21 | 45737.8667 | 0.0012045 | 2.0767e-05 | 13 | 754 | Unplanned | Defective equipment
3488 |  | 38867 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-03-21 | 45737.8611 | 2025-03-21 | 45737.9236 | 0.04748 | 0.0015576 | 975 | 29722 | Unplanned | Cause unknown
3489 |  | 38868 | HOBV K10 - K10 OREIL AVENUE | Northern | HOBV K10 | 2025-03-21 | 45737.8764 | 2025-03-22 | 45738.1403 | 0.027457 | 0.0006901 | 229 | 17188 | Planned | Planned
3490 |  | 38869 | NEWM K12 - K12 SUITER ST LION BUILDING | Auckland | NEWM K12 | 2025-03-22 | 45738.0208 | 2025-03-22 | 45738.1181 | 0.00022364 | 1.597e-06 | 1 | 140 | Planned | Planned
3491 |  | 38870 | RANU K02 - K02 ZITA MARIA | Northern | RANU K02 | 2025-03-22 | 45738.3542 | 2025-03-22 | 45738.591 | 0.064823 | 0.0001901 | 119 | 40579 | Planned | Planned
3492 |  | 38871 | WOOD K06 - K06 POMARIA RD | Northern | WOOD K06 | 2025-03-22 | 45738.3542 | 2025-03-22 | 45738.6139 | 0.033457 | 8.9458e-05 | 56 | 20944 | Planned | Planned
3493 |  | 38872 | MEAS K19 - K19 STATION RD | Auckland | MEAS K19 | 2025-03-22 | 45738.3806 | 2025-03-22 | 45738.7417 | 0.0099042 | 1.9167e-05 | 12 | 6200 | Planned | Planned
3494 |  | 38873 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2025-03-22 | 45738.4194 | 2025-03-22 | 45738.8403 | 0.023232 | 3.8339e-05 | 24 | 14543 | Planned | Planned
3495 |  | 38875 | QUAY J03 - J03 GOLDEN BAY CEMENT | Auckland | QUAY J03 | 2025-03-22 | 45738.875 | 2025-03-22 | 45738.8854 | 2.3962e-05 | 1.597e-06 | 1 | 15 | Planned | Planned
3496 |  | 38876 | BRIC K10 - K10 ASTLEY AVE | Northern | BRIC K10 | 2025-03-22 | 45738.8646 | 2025-03-22 | 45738.8958 | 0.00093451 | 2.0767e-05 | 13 | 585 | Unplanned | Defective equipment
3497 |  | 38877 | REMU K12 - K12 PEACH PARADE | Auckland | REMU K12 | 2025-03-23 | 45739.9583 | 2025-03-24 | 45740.0403 | 0.01885 | 0.00015975 | 100 | 11800 | Planned | Planned
3498 |  | 38878 | REMU K18 - K18 HAAST ST | Auckland | REMU K18 | 2025-03-24 | 45740.0833 | 2025-03-24 | 45740.159 | 0.032387 | 0.00029713 | 186 | 20274 | Planned | Planned
3499 |  | 38879 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-03-24 | 45740.1111 | 2025-03-24 | 45740.2306 | 0.0065943 | 3.8336e-05 | 24 | 4128 | Unplanned | Wildlife
3500 |  | 38880 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-03-24 | 45740.3403 | 2025-03-24 | 45740.6306 | 0.02671 | 6.3898e-05 | 40 | 16720 | Unplanned | Third party interference
3501 |  | 38881 | SWAN K07 - K07 BETHELLS | Northern | SWAN K07 | 2025-03-24 | 45740.3958 | 2025-03-24 | 45740.7042 | 0.025534 | 5.7508e-05 | 36 | 15984 | Planned | Planned
3502 |  | 38882 | KING K02 - K02 KINGSLAND AVE | Auckland | KING K02 | 2025-03-24 | 45740.4819 | 2025-03-24 | 45740.6549 | 0.087216 | 0.0015272 | 956 | 54597 | Unplanned | Wildlife
3503 |  | 38883 | WAIR K04 - K04 HILLSIDE ROAD | Northern | WAIR K04 | 2025-03-24 | 45740.6729 | 2025-03-26 | 45742.684 | 0.0046262 | 1.597e-06 | 1 | 2896 | Unplanned | Defective equipment
3504 |  | 38884 | WELL K08 - K08 WHANGARIPO | Northern | WELL K08 | 2025-03-24 | 45740.7597 | 2025-03-24 | 45740.8347 | 0.0013802 | 1.278e-05 | 8 | 864 | Unplanned | Cause unknown
3505 |  | 38885 | MKAU K19 - K19 DIORELLA DRIVE | Auckland | MKAU K19 | 2025-03-24 | 45740.9583 | 2025-03-25 | 45741.0542 | 0.048058 | 0.00034825 | 218 | 30084 | Planned | Planned
3506 |  | 38886 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-03-24 | 45740.925 | 2025-03-24 | 45740.9882 | 0.08149 | 0.0015575 | 975 | 51012 | Unplanned | Cause unknown
3507 |  | 38887 | SHOW K10 - K10 CULVER TERRACE | Auckland | SHOW K10 | 2025-03-25 | 45741.1042 | 2025-03-25 | 45741.1771 | 0.043275 | 0.00041214 | 258 | 27090 | Planned | Planned
3508 |  | 38888 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2025-03-25 | 45741.3799 | 2025-03-25 | 45741.5396 | 0.0099202 | 4.3132e-05 | 27 | 6210 | Planned | Planned
3509 |  | 38889 | FBSH K13 - K13 21 HADDINGTON DR | Auckland | FBSH K13 | 2025-03-25 | 45741.375 | 2025-03-25 | 45741.5597 | 0.033994 | 0.00012779 | 80 | 21280 | Planned | Planned
3510 |  | 38890 | ATKI K05 - K05 WEST LYNN | Northern | ATKI K05 | 2025-03-25 | 45741.375 | 2025-03-25 | 45741.5618 | 0.1143 | 0.00042492 | 266 | 71554 | Planned | Planned
3511 |  | 38892 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2025-03-25 | 45741.5201 | 2025-03-25 | 45741.5875 | 0.028333 | 0.0015703 | 983 | 17736 | Unplanned | Cause unknown
3512 |  | 38893 | HOBV K04 - K04 ELIZABETH DR | Northern | HOBV K04 | 2025-03-25 | 45741.6743 | 2025-03-25 | 45741.7236 | 0.014051 | 0.001607 | 1006 | 8796 | Unplanned | Defective equipment
3513 |  | 38895 | WELL K02 - K02 TOMARATA | Northern | WELL K02 | 2025-03-25 | 45741.7715 | 2025-03-25 | 45741.8097 | 0.00052716 | 9.585e-06 | 6 | 330 | Unplanned | Cause unknown
3514 |  | 38896 | SHOW K05 - K05 LITTEN RD | Auckland | SHOW K05 | 2025-03-25 | 45741.9583 | 2025-03-26 | 45742.1715 | 0.14664 | 0.00047764 | 299 | 91793 | Planned | Planned
3515 |  | 38897 | MANL K11 - K11 SCOTTS ROAD | Northern | MANL K11 | 2025-03-26 | 45742.2083 | 2025-03-26 | 45742.9424 | 0.0014058 | 3.195e-05 | 10 | 880 | Planned | Planned
3516 |  | 38898 | WAIM K09 - K09 TAPU ROAD | Northern | WAIM K09 | 2025-03-26 | 45742.334 | 2025-03-26 | 45742.8833 | 0.15416 | 0.00019489 | 122 | 96502 | Planned | Planned
3517 |  | 38899 | SHEL K06 - K06 RIDDELL RD EAST | Auckland | SHEL K06 | 2025-03-26 | 45742.3313 | 2025-03-26 | 45742.5903 | 0.0023834 | 6.39e-06 | 4 | 1492 | Planned | Planned
3518 |  | 38900 | SPUR K05 - K05 DAIRY FLAT | Northern | SPUR K05 | 2025-03-26 | 45742.3569 | 2025-03-26 | 45742.7069 | 0.17874 | 0.00035463 | 222 | 111888 | Planned | Planned
3519 |  | 38901 | BOMA K01 - K01 TAWHARANUI | Northern | BOMA K01 | 2025-03-26 | 45742.3542 | 2025-03-26 | 45742.7201 | 0.20373 | 0.00038658 | 242 | 127534 | Planned | Planned
3520 |  | 38902 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2025-03-26 | 45742.4 | 2025-03-26 | 45742.7486 | 0.075103 | 0.00015016 | 94 | 47014 | Planned | Planned
3521 |  | 38903 | TAKA K12 - K12 MILL RD | Auckland | TAKA K12 | 2025-03-26 | 45742.375 | 2025-03-26 | 45742.575 | 0.0066902 | 4.952e-05 | 31 | 4188 | Unplanned | Defective equipment
3522 |  | 38904 | SWAN K09 - K09 LUANDA DR | Northern | SWAN K09 | 2025-03-26 | 45742.5 | 2025-03-26 | 45742.5104 | 4.7924e-05 | 3.195e-06 | 2 | 30 | Planned | Planned
3523 |  | 38905 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2025-03-26 | 45742.375 | 2025-03-26 | 45742.6708 | 0.019735 | 4.6326e-05 | 29 | 12354 | Planned | Planned
3524 |  | 38906 | TATA K04 - K04 HARBOUR VIEW | Northern | TATA K04 | 2025-03-26 | 45742.7257 | 2025-03-26 | 45742.7569 | 0.0025879 | 5.7509e-05 | 36 | 1620 | Unplanned | Defective equipment
3525 |  | 38907 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-03-26 | 45742.8306 | 2025-03-26 | 45742.9 | 0.00031949 | 3.195e-06 | 2 | 200 | Unplanned | Wildlife
3526 |  | 38908 | WELL K07 - K07 TE HANA | Northern | WELL K07 | 2025-03-26 | 45742.8917 | 2025-03-27 | 45743.2403 | 0.063381 | 0.0027684 | 1733 | 39676 | Unplanned | Third party interference
3527 |  | 38909 | TPAP K16 - K16 MAYS RD | Auckland | TPAP K16 | 2025-03-26 | 45742.9694 | 2025-03-27 | 45743.0229 | 0.031612 | 0.00041055 | 257 | 19789 | Unplanned | Vegetation
3528 |  | 38910 | MILF K03 - K03 KITCHENER ROAD | Northern | MILF K03 | 2025-03-26 | 45742.9583 | 2025-03-27 | 45743.1118 | 0.020829 | 9.425e-05 | 59 | 13039 | Planned | Planned
3529 |  | 38911 | NEWM K01 - K01 EDUCATIONAL DEPT VIA LS | Auckland | NEWM K01 | 2025-03-26 | 45742.9625 | 2025-03-27 | 45743.05 | 0.062195 | 0.00049361 | 309 | 38934 | Planned | Planned
3530 |  | 38912 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2025-03-27 | 45743.0229 | 2025-03-27 | 45743.5938 | 0.10171 | 0.00032107 | 201 | 63671 | Unplanned | Cause unknown
3531 |  | 38913 | ORAK K04 - K04 HAWERA RD | Auckland | ORAK K04 | 2025-03-27 | 45743.0931 | 2025-03-27 | 45743.1896 | 0.071277 | 0.00051278 | 321 | 44619 | Planned | Planned
3532 |  | 38914 | WAIH K05 - K05 PUTIKI RD | Auckland | WAIH K05 | 2025-03-27 | 45743.3924 | 2025-03-27 | 45743.6507 | 0.041598 | 0.00011182 | 70 | 26040 | Planned | Planned
3533 |  | 38916 | GULF K12 - K12 BLUE VISTA ROAD | Northern | GULF K12 | 2025-03-27 | 45743.3854 | 2025-03-27 | 45743.6438 | 0.11469 | 0.00030831 | 193 | 71796 | Planned | Planned
3534 |  | 38917 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2025-03-27 | 45743.375 | 2025-03-27 | 45743.6181 | 0.0016773 | 4.792e-06 | 3 | 1050 | Planned | Planned
3535 |  | 38919 | WARK K05 - K05 SATELLITE | Northern | WARK K05 | 2025-03-27 | 45743.5958 | 2025-03-27 | 45743.6007 | 3.3547e-05 | 4.792e-06 | 3 | 21 | Unplanned | Other Cause | Outage caused by Tap Operation
3536 |  | 38920 | BOMA - Big Omaha | Northern | BOMA K01 | 2025-03-27 | 45743.9007 | 2025-03-27 | 45743.9743 | 0.20469 | 0.003992 | 2499 | 128135 | Unplanned | Cause unknown
3537 |  | 38920 | BOMA - Big Omaha | Northern | BOMA K04 | 2025-03-27 | 45743.9007 | 2025-03-27 | 45743.9743 | 0.12295 | 0.0015143 | 948 | 76968 | Unplanned | Cause unknown
3538 |  | 38920 | BOMA - Big Omaha | Northern | BOMA K06 | 2025-03-27 | 45743.9007 | 2025-03-27 | 45743.9743 | 0.00016614 | 1.596e-06 | 1 | 104 | Unplanned | Cause unknown
3539 |  | 38921 | WARK K04 - K04 LIME WORKS | Northern | WARK K04 | 2025-03-27 | 45743.9167 | 2025-03-28 | 45744.0229 | 0.0046438 | 3.0352e-05 | 19 | 2907 | Planned | Planned
3540 |  | 38922 | TAKA K16 - K16 BERWYN AVE | Auckland | TAKA K16 | 2025-03-27 | 45743.9583 | 2025-03-28 | 45744.0382 | 0.024433 | 0.00021246 | 133 | 15295 | Planned | Planned
3541 |  | 38923 | NEWT K18 - K18 SYMONDS ST 226 | Auckland | NEWT K18 | 2025-03-28 | 45744.0215 | 2025-03-28 | 45744.0819 | 0.01904 | 0.00021885 | 137 | 11919 | Planned | Planned
3542 |  | 38924 | OREW K02 - K02 WAIWERA | Northern | OREW K02 | 2025-03-28 | 45744.3819 | 2025-03-28 | 45744.6562 | 0.003786 | 9.585e-06 | 6 | 2370 | Unplanned | Vegetation
3543 |  | 38926 | WELL K09 - K09 PORT ALBERT | Northern | WELL K09 | 2025-03-28 | 45744.425 | 2025-03-28 | 45744.65 | 0.023809 | 7.3481e-05 | 46 | 14904 | Planned | Planned
3544 |  | 38927 | CLEV R140 - CLEVEDON 3150 R140 | Auckland | CLEV R140 | 2025-03-28 | 45744.5486 | 2025-03-28 | 45744.7014 | 0.10106 | 0.001147 | 718 | 63264 | Unplanned | Human error
3545 |  | 38928 | HPOI K02 - K02 SQUADRON DRV | Northern | HPOI K02 | 2025-03-28 | 45744.9583 | 2025-03-28 | 45744.9757 | 0.00015975 | 6.389e-06 | 4 | 100 | Planned | Planned
3546 |  | 38929 | SAND K14 - K14 2 WAITE AVE | Auckland | SAND K14 | 2025-03-29 | 45745.1389 | 2025-03-29 | 45745.2708 | 0.080153 | 0.0015176 | 475 | 50175 | Unplanned | Defective equipment
3547 |  | 38930 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2025-03-29 | 45745.2583 | 2025-03-29 | 45745.7812 | 0.098499 | 0.00017572 | 109 | 61660 | Planned | Planned
3548 |  | 38931 | WAIH K06 - K06 ONETANGI RD VIA LS | Auckland | WAIH K06 | 2025-03-29 | 45745.3708 | 2025-03-31 | 45747.5951 | 0.081999 | 0.0019952 | 1221 | 51331 | Unplanned | Defective equipment
3549 |  | 38932 | NGAT K02 - K02 STANLEY POINT | Northern | NGAT K02 | 2025-03-29 | 45745.5514 | 2025-03-29 | 45745.6097 | 0.056895 | 0.00067732 | 424 | 35616 | Unplanned | Cause unknown
3550 |  | 38933 | MANL K02 - K02 STANMORE BAY | Northern | MANL K02 | 2025-03-29 | 45745.8125 | 2025-03-30 | 45746.0118 | 0.18838 | 0.0017668 | 1106 | 117922 | Unplanned | Defective equipment
3551 |  | 38934 | KEEL K11 - K11 UTILITECH | Northern | KEEL K11 | 2025-03-30 | 45746.4875 | 2025-03-30 | 45746.5708 | 0.0042173 | 3.5144e-05 | 22 | 2640 | Unplanned | Defective equipment
3552 |  | 38935 | KKAP K04 - K04 GLORIT | Northern | KKAP K04 | 2025-03-30 | 45746.2896 | 2025-03-30 | 45746.7257 | 0.00081151 | 3.196e-06 | 1 | 508 | Unplanned | Defective equipment
3553 |  | 38939 | ORAK K05 - K05 GODDEN CRES | Auckland | ORAK K05 | 2025-03-30 | 45746.9236 | 2025-03-31 | 45747.1819 | 0.0083196 | 2.2364e-05 | 14 | 5208 | Planned | Planned
3554 |  | 38940 | HELE K02 - K02 OLD NORTH ROAD | Northern | HELE K02 | 2025-03-30 | 45746.8819 | 2025-03-30 | 45746.9722 | 0.00041534 | 3.194e-06 | 2 | 260 | Unplanned | Cause unknown
3555 |  | 38943 | WAIM K08 - K08 SCHOOL ROAD | Northern | WAIM K08 | 2025-03-30 | 45746.8403 | 2025-03-31 | 45747.3799 | 0.0049649 | 6.389e-06 | 4 | 3108 | Unplanned | Wildlife
3556 |  | 38944 | BIRK K04 - K04 LEVESQUE STREET | Northern | BIRK K04 | 2025-03-31 | 45747.3958 | 2025-03-31 | 45747.7146 | 0.067585 | 0.00015016 | 94 | 42308 | Planned | Planned
3557 |  | 38945 | WELL K03 - K03 WAYBY | Northern | WELL K03 | 2025-03-31 | 45747.3958 | 2025-03-31 | 45747.6319 | 0.00054314 | 1.597e-06 | 1 | 340 | Planned | Planned
3558 |  | 38946 | BOMA K04 - K04 WHANGATEAU NORTH | Northern | BOMA K04 | 2025-03-31 | 45747.3847 | 2025-03-31 | 45747.4431 | 0.00053675 | 6.39e-06 | 4 | 336 | Planned | Planned
3559 |  | 38948 | MARA K01 - K01 BEACHLANDS | Auckland | MARA K01 | 2025-03-31 | 45747.5632 | 2025-03-31 | 45747.7667 | 0.013574 | 4.6326e-05 | 29 | 8497 | Unplanned | Human error
3560 |  | 39683 | COAT K11 - K11 WAKE ROAD | Northern | COAT K11 | 2024-05-29 | 45441.884 | 2024-05-30 | 45442.4208 | 0.0061742 | 7.987e-06 | 5 | 3865 | Unplanned | Adverse weather | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
3561 |  | 39684 | HELE K09 - K09 WOODHILL | Northern | HELE K09 | 2024-05-30 | 45442.3278 | 2024-05-30 | 45442.6354 | 0.014861 | 3.3547e-05 | 21 | 9303 | Unplanned | Cause unknown | The interruptions occurred during the storm that hit the North Island on the 28th and 29th of May 2024, with gusts exceeding 120 km/h
3562 |  | 39685 | WARK K12 - K12 MATAKANA | Northern | WARK K12 | 2024-09-01 | 45536.4632 | 2024-09-01 | 45536.5347 | 0.00032908 | 3.194e-06 | 2 | 206 | Unplanned | Cause unknown
3563 |  | 39686 | LAIN K03 - K03 PARAU PUMPS | Northern | LAIN K03 | 2024-10-06 | 45571.4583 | 2024-10-06 | 45571.6597 | 0.0032428 | 1.1182e-05 | 7 | 2030 | Unplanned | Cause unknown
28